## 1
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-01
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 71 | 71.9 |  | 76 |  | 74 |  | 69.7 | 77.3 | 76.5 |  | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 66.9 | 66.4 |  | 71.3 |  | 69.1 |  | 65.3 | 73.2 | 71.6 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 62.9 | 67.8 |  | 70.6 |  | 63.8 |  | 65.2 | 69.2 | 74.2 |  | 73.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 37.9 | 37.3 |  | 52.2 |  | 38.2 |  | 32.1 | 54.6 | 53.5 |  | 42
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 116.9 | 117.5 |  | 115.6 |  | 116.4 |  | 112.3 | 118.3 | 118.3 |  | 118.5
| INPUT | Kw | 1194kW | 1139 | 1158 |  | 1171 |  | 1182 |  | 1140 | 1202 | 1202 |  | 1205
COMPRESSOR | RUNNING TIME | Hr | NA | 49728.5 | 49721.3 |  | 50996.4 |  | 48658 |  | 51039.1 | 50216.4 | 50207.5 |  | 50357.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 59 |  | 58.9 |  | 57.8 |  | 57.2 | 58.6 | 58.5 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  | 0.59 |  | 0.52 | 0.47 | 0.47 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 45 |  | 45.2 |  | 44.8 |  | 45.2 | 44.9 | 45.1 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.8 | 4.4 |  | 3.5 |  | 4.2 |  | 3.7 | 4 | 4.1 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 3.3 | 3.8 |  | 2.7 |  | 3.5 |  | 2.7 | 2.8 | 3.3 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 1 | 1 | 0 | 2.1 | 0 | 0.7 | 0 | 1.1 | 1.3 | 1.1 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 701.5 | 673 |  | 652.6 |  | 634.3 |  | 643.3 | 684.7 | 652.8 |  | 643
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.6 | 13.4 |  | 13.6 |  | 13.4 |  | 12.8 | 12.6 | 13.6 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 4.8 |  | 4.8 |  | 4.2 |  | 3.8 | 4.1 | 4.4 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.3 | 8.6 | 0 | 8.8 | 0 | 9.2 | 0 | 9 | 8.5 | 9.2 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 6723.3834 | 6683.3718 | 0 | 6631.5012 | 0 | 6738.5219 | 0 | 6685.5658 | 6720.4965 | 6935.0577 | 0 | 6385.4503
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.82 |  | 0.84 |  | 0.82 |  | 0.81 | 0.8 | 0.82 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.7 | 36 |  | 36.2 |  | 36 |  | 35.7 | 35.5 | 35.3 |  | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C | 36.2 | 36.4 |  | 37.2 |  | 36.7 |  | 36.2 | 35.9 | 35.7 |  | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.1 | 2.1 | 1 | 3.8 | 0 | 2.4 | 0 | 2.5 | 1.7 | 1.6 | 0 | 3.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.5 | 28 |  | 28.2 |  | 28.3 |  | 28.2 | 28.7 | 28 |  | 27.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.1 | 34.3 |  | 33.4 |  | 34.3 |  | 33.7 | 34.2 | 34.1 |  | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 6.3 | 0 | 5.2 | 0 | 6 | 0 | 5.5 | 5.5 | 6.1 | 0 | 6
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1259.2 | 1155.8 |  | 1149.9 |  | 1177.2 |  | 1151.4 | 1271.8 | 1138.6 |  | 1165.7
| HEAT CAPACITY | kW | 8226.9 | 8142.6328 | 8408.2448 | 0 | 6904.7113 | 0 | 8156.1201 | 0 | 7312.5866 | 8077.2517 | 8020.1617 | 0 | 8076.4434
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.47 |  | 0.46 |  | 0.46 |  | 0.46 | 0.45 | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.5 | 19.9 |  | 19.4 |  | 19.6 |  | 19.5 | 18.7 | 19.1 |  | 20.1
| LIQUID LEVEL | mm | mm | 193.1 | 196.9 |  | 120.4 |  | 205 |  | 195.4 | 155.3 | 159.9 |  | 195.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.85 | 5.6 |  | 5.5 |  | 5.72 |  | 5.72 | 5.25 | 5.64 |  | 5.26
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 2
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-02
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.5 |  | 83.1 | 72 | 74.7 | 78 | 74 |  | 77.3 |  | 75.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.8 |  | 0 | 0 | 0 | 0 | 0 |  | 0.2 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66 |  | 79 | 69 | 71.1 | 73.3 | 69.6 |  | 73.2 |  | 70.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 68.1 |  | 69.3 | 62 | 64.4 | 64.8 | 66.2 |  | 75.1 |  | 73.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 38 |  | 52.5 | 39.6 | 40.9 | 73.3 | 33.9 |  | 55.9 |  | 45
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 118.5 |  | 120 | 116.7 | 118.7 | 120.5 | 116.6 |  | 119.9 |  | 119.7
| INPUT | Kw | 1194kW |  | 1164 |  | 1210 | 1179 | 1197 | 1216 | 1177 |  | 1213 |  | 1206
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49738.2 |  | 51004.3 | 48675.6 | 48665.1 | 51058.1 | 51047.6 |  | 50226.7 |  | 50365.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 |  | 59.4 | 57.8 | 57.8 | 57.5 | 57.3 |  | 58.5 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.58 | 0.52 | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 |  | 45 | 44.9 | 45 | 44.8 | 45.1 |  | 45.1 |  | 45.2
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.22 | 0.22 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.2 | 4.3 | 4 | 4.1 | 3.8 |  | 4 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.3 | 3.1 | 3.2 | 3.1 | 2.8 |  | 3.2 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | 2.7 | 1.1 | 0.7 | 1 | 1.3 | 0 | 1.4 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 666.9 |  | 649.5 | 680.65 | 643.4 | 709.4 | 637.1 |  | 655.8 |  | 642.5
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.8 |  | 13.9 | 12.8 | 13.1 | 12.8 | 13.3 |  | 14 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 |  | 5 | 4.2 | 3.9 | 4.1 | 4.1 |  | 4.6 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9 | 0 | 8.9 | 8.6 | 9.2 | 8.7 | 9.2 | 0 | 9.4 | 0 | 9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6930.8314 | 0 | 6675 | 6759.3418 | 6835.1963 | 7126.7667 | 6768.2679 | 0 | 7118.3834 | 0 | 6677.2517
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 |  | 0.83 | 0.82 | 0.82 | 0.82 | 0.81 |  | 0.82 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.6 |  | 36.3 | 35.8 | 35.8 | 36 | 35.5 |  | 34.9 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.1 |  | 37.1 | 36.6 | 36.4 | 36.5 | 36.1 |  | 35.5 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.2 | 1 | 3.7 | 2.5 | 2.4 | 2.6 | 2.7 | 0 | 1.8 | 0 | 3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.4 |  | 28.3 | 28.7 | 28.5 | 28.5 | 28.4 |  | 28.3 |  | 28.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.9 |  | 33.4 | 34.1 | 34 | 33.9 | 33.4 |  | 33.7 |  | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 5.1 | 5.4 | 5.5 | 5.4 | 5 | 0 | 5.4 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1290.7 |  | 1280.1 | 1296.4 | 1292.1 | 1299.8 | 1298.4 |  | 1286.6 |  | 1294.3
| HEAT CAPACITY | kW | 8226.9 | 0 | 8197.2864 | 0 | 7538.6952 | 8083.7875 | 8206.1778 | 8104.9885 | 7496.5358 | 0 | 8022.679 | 0 | 7921.2356
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.7 |  | 19.1 | 19.4 | 19.2 | 19.6 | 19.3 |  | 18.9 |  | 19.8
| LIQUID LEVEL | mm | mm |  | 214.4 |  | 125 | 196.7 | 200.9 | 201 | 211.1 |  | 158.7 |  | 195.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.71 |  | 5.39 | 5.4 | 5.65 | 5.11 | 5.67 |  | 5.78 |  | 5.46
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 3
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-03
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.1 | 71.5 |  | 83.1 |  | 74.7 |  | 74 | 79.6 | 77.3 |  | 75.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.8 |  | 0 |  | 0 |  | 0 | 0 | 0.2 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.3 | 66 |  | 79 |  | 71.1 |  | 69.6 | 75.3 | 73.2 |  | 70.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 65.3 | 68.1 |  | 69.3 |  | 64.4 |  | 66.2 | 71 | 75.1 |  | 73.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 37.3 | 38 |  | 52.5 |  | 40.9 |  | 33.9 | 55.8 | 55.9 |  | 45
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118.8 | 118.5 |  | 120 |  | 118.7 |  | 116.6 | 120.2 | 119.9 |  | 119.7
| INPUT | Kw | 1194kW | 1170 | 1164 |  | 1210 |  | 1197 |  | 1177 | 1227 | 1213 |  | 1206
COMPRESSOR | RUNNING TIME | Hr | NA | 49757.4 | [7 empty] | 50247
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.8 | 58.4 |  | 59.4 |  | 57.8 |  | 57.3 | 58.6 | 58.5 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.58 |  | 0.52 | 0.47 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.8 | 45 |  | 45 |  | 45 |  | 45.1 | 44.9 | 45.1 |  | 45.2
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.21 |  | 0.22 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.2 | 4.4 |  | 3.2 |  | 4 |  | 3.8 | 4.2 | 4 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C | 3.7 | 3.8 |  | 2.3 |  | 3.2 |  | 2.8 | 3.7 | 3.2 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 1.1 | 1 | 0 | 2.7 | 0 | 0.7 | 0 | 1.3 | 0.8 | 1.4 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 696.2 | 666.9 |  | 649.5 |  | 643.4 |  | 637.1 | 685.8 | 655.8 |  | 642.5
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.4 | 13.8 |  | 13.9 |  | 13.1 |  | 13.3 | 13.4 | 14 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.8 | 4.8 |  | 5 |  | 3.9 |  | 4.1 | 4.5 | 4.6 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.6 | 9 | 0 | 8.9 | 0 | 9.2 | 0 | 9.2 | 8.9 | 9.4 | 0 | 9
| CHILLING CAPACITY | kW | 7032.6kW | 6913.7644 | 6930.8314 | 0 | 6675 | 0 | 6835.1963 | 0 | 6768.2679 | 7048.06 | 7118.3834 | 0 | 6677.2517
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.81 |  | 0.83 |  | 0.82 |  | 0.81 | 0.8 | 0.82 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.8 | 35.6 |  | 36.3 |  | 35.8 |  | 35.5 | 35 | 34.9 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C | 36.2 | 36.1 |  | 37.1 |  | 36.4 |  | 36.1 | 35.6 | 35.5 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.1 | 2.2 | 1 | 3.7 | 0 | 2.4 | 0 | 2.7 | 1.7 | 1.8 | 0 | 3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.6 | 28.4 |  | 28.3 |  | 28.5 |  | 28.4 | 28.4 | 28.3 |  | 28.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.1 | 33.9 |  | 33.4 |  | 34 |  | 33.4 | 33.9 | 33.7 |  | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.5 | 0 | 5.1 | 0 | 5.5 | 0 | 5 | 5.5 | 5.4 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1296.6 | 1290.7 |  | 1280.1 |  | 1292.1 |  | 1298.4 | 1292.6 | 1286.6 |  | 1294.3
| HEAT CAPACITY | kW | 8226.9 | 8234.7575 | 8197.2864 | 0 | 7538.6952 | 0 | 8206.1778 | 0 | 7496.5358 | 8209.3533 | 8022.679 | 0 | 7921.2356
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.46 |  | 0.46 |  | 0.46 |  | 0.46 | 0.45 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.6 | 19.7 |  | 19.1 |  | 19.2 |  | 19.3 | 18.7 | 18.9 |  | 19.8
| LIQUID LEVEL | mm | mm | 202 | 214.4 |  | 125 |  | 200.9 |  | 211.1 | 162 | 158.7 |  | 195.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.44 | 5.71 |  | 5.39 |  | 5.65 | 5.11 | 5.67 | 5.37 | 5.78 |  | 5.46
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 4
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-04
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.9 |  | 83.1 | 74.9 | 74 | 71.8 | 69.7 |  | 77.3 |  | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 |  | 0 | 0 | 0 | 0.1 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.4 |  | 71.3 | 69.1 | 69.1 | 68.7 | 65.3 |  | 71.6 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.8 |  | 70.6 | 62.8 | 63.8 | 65.5 | 65.2 |  | 74.2 |  | 73.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.3 |  | 52.2 | 37.8 | 38.2 | 31.2 | 32.1 |  | 53.5 |  | 42
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.5 |  | 115.6 | 117.4 | 116.4 | 114.4 | 112.3 |  | 118.3 |  | 118.5
| INPUT | Kw | 1194kW |  | 1158 |  | 1171 | 1198 | 1182 | 1164 | 1140 |  | 1202 |  | 1205
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49765.6 |  | 51023.3 | 48703.6 | 48694.9 | 51086 | 51077.3 |  | 50255.4 |  | 50384.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 59 |  | 58.9 | 58 | 57.8 | 57.5 | 57.2 |  | 58.5 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.47 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 |  | 45.2 | 45.3 | 44.8 | 45 | 45.2 |  | 45.1 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.5 | 4.3 | 4.2 | 3.7 | 3.7 |  | 4.1 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.7 | 3.4 | 3.5 | 2.6 | 2.7 |  | 3.3 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 0.7 | 0 | 2.1 | 0.7 | 1.1 | 1.3 | 1.1 | 0 | 0.9 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 639.28 |  | 640.16 | 655.9 | 640.88 | 629.9 | 636.58 |  | 629.44 |  | 643.36
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.5 | 13 | 13.5 | 12.8 | 12.9 |  | 13.4 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.5 |  | 4.8 | 4.1 | 4.6 | 3.9 | 3.8 |  | 4.2 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9 | 0 | 8.7 | 8.9 | 8.9 | 8.9 | 9.1 | 0 | 9.2 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6643.7875 | 0 | 6431.1686 | 6740.7737 | 6586.4111 | 6473.5681 | 6689.2356 | 0 | 6686.8915 | 0 | 6463.3164
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 |  | 0.84 | 0.83 | 0.82 | 0.82 | 0.81 |  | 0.79 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 |  | 36.2 | 36.3 | 36 | 36.2 | 35.7 |  | 35.3 |  | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.6 |  | 37 | 37.1 | 36.5 | 36.6 | 35.9 |  | 35.2 |  | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.3 | 1 | 4.1 | 2.7 | 3.2 | 2.6 | 3.2 | 0 | 2.4 | 0 | 3.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28 |  | 27.9 | 28.9 | 27.9 | 28.8 | 27.7 |  | 27.8 |  | 28.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.3 |  | 32.9 | 34.4 | 33.3 | 34 | 32.7 |  | 32.8 |  | 33.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 0 | 5 | 5.5 | 5.4 | 5.2 | 5 | 0 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1294.72 |  | 1277.64 | 1279.3 | 1298.64 | 1290 | 1289.58 |  | 1290.24 |  | 1290.8
| HEAT CAPACITY | kW | 8226.9 | 0 | 7923.806 | 0 | 7376.6744 | 8124.8845 | 8097.7552 | 7745.9584 | 7445.612 | 0 | 7449.4226 | 0 | 7750.7621
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 |  | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.9 |  | 19.4 | 19.8 | 19.6 | 19.5 | 19.5 |  | 19.1 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 196.9 |  | 120.4 | 203.6 | 205 | 200.7 | 195.4 |  | 159.9 |  | 195.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.71 |  | 5.39 | 5.54 | 5.65 | 5.7 | 5.72 |  | 5.78 |  | 5.26
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 5
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-05
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 71.4 | 71.4 |  | 81.3 |  | 72 |  | 70.4 | 77.8 | 78.5 |  | 74.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.4 | 0.4 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 66.5 | 66.3 |  | 77.1 |  | 68.2 |  | 65 | 72.5 | 74.1 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69 | 69.5 |  | 70.4 |  | 64.7 |  | 66.5 | 75.3 | 74.8 |  | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 40.1 | 42 |  | 56 |  | 42.1 |  | 34.9 | 49.5 | 58.2 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 115.2 | 115.9 |  | 116.7 |  | 114.6 |  | 111.9 | 119.5 | 118.9 |  | 116.8
| INPUT | Kw | 1194kW | 1136 | 1125 |  | 1175 |  | 1153 |  | 1133 | 1200 | 1200 |  | 1179
COMPRESSOR | RUNNING TIME | Hr | NA | 49784 | 49775.6 |  | 51033.7 |  | 48713.4 |  | 51098.2 | 50274.2 | 50265.9 |  | 50394.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58 |  | 58.9 |  | 57.7 |  | 57.2 | 58.5 | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.48 |  | 0.58 |  | 0.52 | 0.57 | 0.57 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.7 | 45 |  | 45 |  | 45.1 |  | 45 | 44.9 | 45 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.21 |  | 0.21 |  | 0.23 |  | 0.22 | 0.23 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4 | 3.9 |  | 2.8 |  | 4 |  | 3.9 | 4.4 | 4 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C | 3.6 | 3.3 |  | 2 |  | 3.2 |  | 2.4 | 3.1 | 2.8 |  | 3.1
| APPROACH TEMP | CELCIUS | C | 0.9 | 1 | 0 | 2.6 | 0 | 1.4 | 0 | 1.3 | 1.1 | 1.3 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 629.12 | 656.4 |  | 635.6 |  | 637.4 |  | 624.8 | 632.24 | 642.3 |  | 638.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.7 | 13.3 |  | 13.4 |  | 13.5 |  | 13 | 13.5 | 13.4 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.5 | 4.3 |  | 4.6 |  | 4.6 |  | 3.7 | 4.2 | 4.1 |  | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9.2 | 9 | 0 | 8.8 | 0 | 8.9 | 0 | 9.3 | 9.3 | 9.3 | 0 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW | 6683.4919 | 6821.709 | 0 | 6458.7529 | 0 | 6550.6467 | 0 | 6709.746 | 6789.6443 | 6897.679 | 0 | 6566.0624
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.79 | 0.78 |  | 0.8 |  | 0.8 |  | 0.78 | 0.78 | 0.77 |  | 0.79
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.7 | 34.5 |  | 35 |  | 34.8 |  | 34.7 | 34.3 | 34.1 |  | 34.7
| SATURATED TEMEPRATURE | CELCIUS | C | 35.4 | 35.1 |  | 36 |  | 35.6 |  | 35.1 | 34.9 | 34.7 |  | 35.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.4 | 1.7 | 1 | 3.3 | 0 | 2.2 | 0 | 2.3 | 2.4 | 1.6 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.8 | 27.9 |  | 27.8 |  | 27.2 |  | 27.8 | 27.5 | 27.5 |  | 27.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33 | 33.4 |  | 32.7 |  | 33.4 |  | 32.8 | 32.5 | 33.1 |  | 33
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.2 | 5.5 | 0 | 4.9 | 0 | 6.2 | 0 | 5 | 5 | 5.6 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1292.06 | 1295.8 |  | 1300.6 |  | 1295.8 |  | 1293.1 | 1297.38 | 1285.4 |  | 1296.4
| HEAT CAPACITY | kW | 8226.9 | 7758.3279 | 8229.6767 | 0 | 7359.0531 | 0 | 9277.0901 | 0 | 7465.9353 | 7490.6467 | 8312.0554 | 0 | 8083.7875
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.45 |  | 0.44 |  | 0.45 |  | 0.45 | 0.44 | 0.44 |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C | 19.3 | 18.9 |  | 18.2 |  | 19 |  | 19.1 | 18.5 | 18.1 |  | 18.9
| LIQUID LEVEL | mm | mm | 191.8 | 201.7 |  | 117.8 |  | 200.8 |  | 206.4 | 159.9 | 160 |  | 199.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 6.09 | 6.04 |  | 5.72 |  | 5.9 |  | 6 | 5.93 | 5.68 |  | 5.33
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 7
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-07
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 74.3 | 71.4 |  | 83.2 |  | 73.8 |  | 74.6 | 80.4 | 77.4 |  | 75
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.6 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 70 | 65.9 |  | 80 |  | 70.5 |  | 69.2 | 76.5 | 72.3 |  | 70.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 63.3 | 67.3 |  | 67.9 |  | 65.2 |  | 66.8 | 69.3 | 72.6 |  | 70
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 39.3 | 36.8 |  | 52.2 |  | 41.4 |  | 32.4 | 56.8 | 55.4 |  | 41.1
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118.1 | 114.3 |  | 116.3 |  | 115.9 |  | 114.2 | 119.4 | 116.4 |  | 115.8
| INPUT | Kw | 1194kW | 1167 | 1133 |  | 1193 |  | 1191 |  | 1169 | 1224 | 1194 |  | 1187
COMPRESSOR | RUNNING TIME | Hr | NA | 49811.2 | 49801.9 |  | 51053 |  | 48739.3 |  | 51128.5 | 50306.6 | 50297.4 |  | 50413.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.1 |  | 59.1 |  | 57.7 |  | 57.2 | 58.3 | 58.4 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.48 |  | 0.58 |  | 0.52 | 0.47 | 0.47 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 45.1 |  | 44.9 |  | 45 |  | 44.9 | 45.1 | 45.1 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.22 |  | 0.21 |  | 0.22 |  | 0.22 | 0.22 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.9 | 3.8 |  | 2.6 |  | 4 |  | 3.7 | 3.9 | 3.7 |  | 4.1
| SATURATION TEMPERATURE | CELCIUS | C | 3.2 | 3.2 |  | 1.7 |  | 3 |  | 2.7 | 2.6 | 2.8 |  | 3
| APPROACH TEMP | CELCIUS | C | 1.1 | 0.9 | 0 | 2.5 | 0 | 0.9 | 0 | 1.2 | 1.6 | 1.1 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 692.7 | 652 |  | 639.5 |  | 640.8 |  | 637.2 | 690.9 | 640.7 |  | 639.5
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.7 | 13.2 |  | 13 |  | 13 |  | 13.2 | 12.8 | 13.2 |  | 12.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 4.1 |  | 4.2 |  | 3.9 |  | 3.9 | 4.2 | 3.9 |  | 4.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.4 | 9.1 | 0 | 8.8 | 0 | 9.1 | 0 | 9.3 | 8.6 | 9.3 | 0 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW | 6719.03 | 6851.2702 | 0 | 6498.3834 | 0 | 6733.5797 | 0 | 6842.9099 | 6861.1316 | 6880.4965 | 0 | 6203.0023
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.8 |  | 0.82 |  | 0.81 |  | 0.8 | 0.66 | 0.76 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.9 | 35.1 |  | 35.7 |  | 35.5 |  | 35.4 | 35.3 | 34.7 |  | 35.4
| SATURATED TEMEPRATURE | CELCIUS | C | 36.8 | 35.6 |  | 36.5 |  | 36.2 |  | 35.9 | 35.9 | 35.2 |  | 36.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.2 | 1.7 | 0 | 3.2 | 0 | 2.1 | 0 | 2.3 | 1.6 | 1.6 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29 | 28.6 |  | 28.4 |  | 28.6 |  | 28.5 | 29 | 28.4 |  | 28.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.6 | 33.9 |  | 33.3 |  | 34.1 |  | 33.6 | 34.3 | 33.6 |  | 33.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 5.3 | 0 | 4.9 | 0 | 5.5 | 0 | 5.1 | 5.3 | 5.2 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1296.2 | 1290.1 |  | 1303 |  | 1296.3 |  | 1298.4 | 1293.8 | 1293.7 |  | 1297.6
| HEAT CAPACITY | kW | 8226.9 | 8381.8938 | 7895.5312 | 0 | 7372.6328 | 0 | 8232.8522 | 0 | 7646.4665 | 7918.1755 | 7768.1755 | 0 | 8091.2702
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.45 |  | 0.44 |  | 0.45 |  | 0.45 | 0.45 | 0.44 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.3 | 19.2 |  | 18.8 |  | 19 |  | 19.2 | 18.8 | 18.5 |  | 19.1
| LIQUID LEVEL | mm | mm | 192.9 | 198.8 |  | 132.5 |  | 197.4 |  | 211.5 | 158.2 | 163.7 |  | 198.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.51 | 5.95 |  | 5.47 |  | 5.65 |  | 5.88 | 5.35 | 5.73 |  | 5.22
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 8
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-08
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 74 | 67.8 |  | 76.4 |  | 74.7 |  | 73.4 | 76.1 | 71.9 |  | 71.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.4 | 0.6 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 69 | 60.8 |  | 71.2 |  | 70.1 |  | 68.8 | 70.8 | 65.7 |  | 64.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 62.2 | 69 |  | 69.7 |  | 64.1 |  | 64.3 | 69.1 | 73.3 |  | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 39.8 | 35.9 |  | 49 |  | 36.7 |  | 33.4 | 42 | 40.9 |  | 41.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 116.9 | 115.8 |  | 116.2 |  | 119 |  | 116.4 | 117.2 | 117.5 |  | 116.6
| INPUT | Kw | 1194kW | 1151 | 1138 |  | 1176 |  | 1211 |  | 1178 | 1198 | 1184 |  | 1180
COMPRESSOR | RUNNING TIME | Hr | NA | 49832.2 | 49822.7 |  | 21063 |  | 48749 |  | 51138.5 | 50433.2 | 50316.1 |  | 50423.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.2 |  | 59.1 |  | 58 |  | 57.3 | 58.9 | 59.1 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.5 |  | 0.59 |  | 0.52 | 49 | 0.5 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 44.8 |  | 44.7 |  | 45 |  | 45.1 | 45.1 | 45.2 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.25 |  | 0.22 |  | 0.21 |  | 0.22 | 0.22 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.7 | 4.7 |  | 3.7 |  | 4.4 |  | 4 | 4.4 | 4.9 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 3.2 | 4.1 |  | 2.9 |  | 3.6 |  | 2.9 | 3.4 | 3.9 |  | 4
| APPROACH TEMP | CELCIUS | C | 1.1 | 0.9 | 0 | 2.1 | 0 | 0.9 | 0 | 0.9 | 1 | 1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 696.4 | 653.4 |  | 638.7 |  | 639.4 |  | 641.2 | 674.6 | 638.5 |  | 639.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12..8 | 13.6 |  | 13.7 |  | 13.4 |  | 12.8 | 12.8 | 13.5 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 5 |  | 5 |  | 4.5 |  | 3.8 | 4.4 | 4.9 |  | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | #VALUE! | 8.6 | 0 | 8.7 | 0 | 8.9 | 0 | 9 | 8.4 | 8.6 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | #VALUE! | 6488.7298 | 0 | 6416.5012 | 0 | 6571.2009 | 0 | 6663.7413 | 6543.4642 | 6340.7621 | 0 | 6277.8291
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.83 |  | 0.85 |  | 0.84 |  | 0.83 | 0.82 | 0.84 |  | 0.85
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.5 | 36.4 |  | 37 |  | 36.7 |  | 36.6 | 35.8 | 36.7 |  | 36.8
| SATURATED TEMEPRATURE | CELCIUS | C | 36.1 | 36.8 |  | 37.8 |  | 37.4 |  | 37.1 | 36.5 | 37.4 |  | 37.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 2.1 | 1 | 3.7 | 0 | 2.5 | 0 | 2.7 | 2.5 | 3 | 0 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.8 | 28.7 |  | 28.8 |  | 28.9 |  | 28.8 | 28.7 | 28.6 |  | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.4 | 34.7 |  | 34.1 |  | 34.9 |  | 34.4 | 34 | 34.4 |  | 34.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 6 | 0 | 5.3 | 0 | 6 | 0 | 5.6 | 5.3 | 5.8 | 0 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1258.7 | 1151.9 |  | 1131.6 |  | 1162.4 |  | 1148.2 | 1296.2 | 1145.3 |  | 1156.1
| HEAT CAPACITY | kW | 8226.9 | 8139.3995 | 7980.8314 | 0 | 6925.4965 | 0 | 8053.5797 | 0 | 7424.8499 | 7932.8637 | 7670.6005 | 0 | 7742.933
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.48 |  | 0.47 |  | 0.47 |  | 0.47 | 0.46 | 0.48 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C | 19.3 | 20.5 |  | 20.2 |  | 19.9 |  | 20 | 19.6 | 20.6 |  | 20.7
| LIQUID LEVEL | mm | mm | 204.9 | 193.4 |  | 123.1 |  | 205.5 |  | 211.7 | 196.9 | 204 |  | 209.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.48 | 5.58 |  | 5.5 |  | 5.48 |  | 5.73 | 5.18 | 5.4 |  | 5.36
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 9
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-09
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  |  |  |  | 74.9 |  | 79
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  |  |  |  | 0 |  | 0.1
OPENING OF 2nd VANE |  | % | 0~100% |  |  |  |  | 70.5 |  | 74.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  |  |  |  | 62.2 |  | 65.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  |  |  |  | 39.2 |  | 37.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  |  |  |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  |  |  |  | 116.5 |  | 118.9
| INPUT | Kw | 1194kW |  |  |  |  | 1184 |  | 1213
COMPRESSOR | RUNNING TIME | Hr | NA |  |  |  |  | 48768.5 |  | 51157.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  |  |  |  | 57.5 |  | 57.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  |  |  |  | 0.58 |  | 0.52
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  |  |  |  | 45 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  |  |  |  | 0.23 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  |  |  |  | 3.9 |  | 3.8
| SATURATION TEMPERATURE | CELCIUS | C |  |  |  |  | 3.2 |  | 2.8
| APPROACH TEMP | CELCIUS | C | 0 | 0 | 0 | 0 | 0.8 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  |  |  |  | 680.4 |  | 710.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  |  |  |  | 12.6 |  | 12.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  |  |  |  | 4 |  | 4.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 0 | 0 | 0 | 8.6 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 0 | 0 | 0 | 6756.8591 | 0 | 7059.746 | 0 | 0 | 0 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  |  |  |  | 0.81 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  |  |  |  | 35.6 |  | 35.6
| SATURATED TEMEPRATURE | CELCIUS | C |  |  |  |  | 36.3 |  | 36.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 0 | 0 | 0 | 2.2 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  |  |  |  | 28.6 |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  |  |  |  | 34.1 |  | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 0 | 0 | 0 | 5.5 | 0 | 5.3 | 0 | 0 | 0 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  |  |  |  | 1293.6 |  | 1298.5
| HEAT CAPACITY | kW | 8226.9 | 0 | 0 | 0 | 0 | 8215.7044 | 0 | 7946.94 | 0 | 0 | 0 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  |  |  |  | 0.46 |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C |  |  |  |  | 19.1 |  | 19.2
| LIQUID LEVEL | mm | mm |  |  |  |  | 206.6 |  | 209.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  |  |  |  | 5.41 |  | 5.24
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 10
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-10
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.5 |  | 83.1 | 74 | 74.7 |  | 74 | 75.6 | 77.3 |  | 75.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.8 |  | 0 | 0 | 0 |  | 0 | 0 | 0.2 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66 |  | 79 | 69.4 | 71.1 |  | 69.6 | 71 | 73.2 |  | 70.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 68.1 |  | 69.3 | 63 | 64.4 |  | 66.2 | 71 | 75.1 |  | 73.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 38 |  | 52.5 | 39.2 | 40.9 |  | 33.9 | 55.1 | 55.9 |  | 45
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 118.5 |  | 120 | 116.2 | 118.7 |  | 116.6 | 116.7 | 119.9 |  | 119.7
| INPUT | Kw | 1194kW |  | 1164 |  | 1210 | 1188 | 1197 |  | 1177 | 1198 | 1213 |  | 1206
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49847.8 |  | 51080.8 | 48792.5 | 48781.5 |  | 51166.7 | 50345.2 | 50334.2 |  | 50453
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 |  | 59.4 | 57.5 | 57.8 |  | 57.3 | 58.7 | 58.5 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.58 |  | 0.52 | 0.48 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 |  | 45 | 45 | 45 |  | 45.1 | 44.9 | 45.1 |  | 45.2
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.23 | 0.22 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.2 | 4.3 | 4 |  | 3.8 | 4.2 | 4 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.3 | 3.5 | 3.2 |  | 2.8 | 3.1 | 3.2 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0 | 2.3 | 0.8 | 1.4 | 0 | 0.7 | 1.4 | 1 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 670.48 |  | 649.84 | 682.5 | 646.64 |  | 626.24 | 691.3 | 657.36 |  | 646.08
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13 |  | 13 | 12.8 | 13.5 |  | 12.7 | 12.8 | 12.9 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.6 | 4.3 | 4.6 |  | 3.5 | 4.5 | 4.2 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.4 | 0 | 8.4 | 8.5 | 8.9 | 0 | 9.2 | 8.3 | 8.7 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6503.5012 | 0 | 6303.2979 | 6698.903 | 6645.6074 | 0 | 6652.8961 | 6625.6236 | 6603.963 | 0 | 6341.4319
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.84 | 0.84 | 0.84 |  | 0.82 | 0.81 | 0.81 |  | 0
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.6 |  | 36.3 | 36.5 | 35.8 |  | 35.5 | 35.7 | 34.9 |  | 0.83
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 37.2 | 37.2 | 37 |  | 36.5 | 36.1 | 36 |  | 36.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.4 | 1 | 3.5 | 2.1 | 2.8 | 0 | 3 | 1.5 | 2.4 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.9 |  | 28.7 | 29.7 | 28.8 |  | 28.5 | 29.2 | 28.6 |  | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34 |  | 33.7 | 35.1 | 34.2 |  | 33.5 | 34.6 | 33.6 |  | 34
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 0 | 5 | 5.4 | 5.4 | 0 | 5 | 5.4 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1292.2 |  | 1305.08 | 1286.5 | 1293.88 |  | 1298.92 | 1298.1 | 1296.26 |  | 1296.82
| HEAT CAPACITY | kW | 8226.9 | 0 | 7609.9538 | 0 | 7535.1039 | 8022.0554 | 8068.0739 | 0 | 7499.5381 | 8094.388 | 7484.1801 | 0 | 7786.9099
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.46 | 0.47 | 0.46 |  | 0.46 | 0.46 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.7 |  | 19.1 | 19.9 | 19.2 |  | 19.3 | 19.2 | 18.9 |  | 19.8
| LIQUID LEVEL | mm | mm |  | 214.4 |  | 125 | 207.4 | 200.9 |  | 211.1 | 169 | 158.7 |  | 195.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.71 |  | 5.39 | 5.32 | 5.65 |  | 5.67 | 5.15 | 5.78 |  | 5.46
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 11
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-11
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70 |  | 77.7 |  | 73.5 |  | 71.7 |  | 75.6 |  | 74
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.3 |  | 73.1 |  | 68.2 |  | 68.9 |  | 71 |  | 68.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66 |  | 68.4 |  | 63.9 |  | 65.2 |  | 72 |  | 72.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 35.4 |  | 49 |  | 36.7 |  | 31.5 |  | 42.3 |  | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.9 |  | 114.7 |  | 115.4 |  | 113.9 |  | 118 |  | 117.4
| INPUT | Kw | 1194kW |  | 1155 |  | 1175 |  | 1194 |  | 1172 |  | 1205 |  | 1201
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49857.6 |  | 51091.1 |  | 48802.1 |  | 51176.9 |  | 50358.6 |  | 50462.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.6 |  | 59 |  | 58 |  | 57.6 |  | 58.7 |  | 59.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 |  | 0.59 |  | 0.52 |  | 0.53 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.7 |  | 45.1 |  | 45 |  | 44.8 |  | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.6 |  | 4.4 |  | 4 |  | 4.2 |  | 4.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.5 |  | 3.5 |  | 2.8 |  | 3.2 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0 | 2.1 | 0 | 1.1 | 0 | 1.1 | 0 | 1.1 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 668.72 |  | 649.76 |  | 635.44 |  | 639.28 |  | 656.32 |  | 649.12
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.9 |  | 13.1 |  | 13.5 |  | 12.9 |  | 13 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.6 |  | 4.6 |  | 3.9 |  | 4.3 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.3 | 0 | 8.5 | 0 | 8.9 | 0 | 9 | 0 | 8.7 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6409.2102 | 0 | 6377.552 | 0 | 6530.5035 | 0 | 6643.7875 | 0 | 6593.515 | 0 | 6446.2263
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 |  | 0.84 |  | 0.83 |  | 0.82 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 |  | 36.6 |  | 36.6 |  | 36.6 |  | 35.9 |  | 36.7
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.8 |  | 37.6 |  | 37.3 |  | 36.9 |  | 36.4 |  | 37.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.4 | 0 | 3.6 | 0 | 2.9 | 0 | 2.9 | 0 | 2.4 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.3 |  | 29.1 |  | 29.2 |  | 29 |  | 29 |  | 29.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.4 |  | 34 |  | 34.4 |  | 34 |  | 34 |  | 34.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 0 | 4.9 | 0 | 5.2 | 0 | 5 | 0 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1297.24 |  | 1296.96 |  | 1290.66 |  | 1295.42 |  | 1294.44 |  | 1296.26
| HEAT CAPACITY | kW | 8226.9 | 0 | 7639.6351 | 0 | 7338.4573 | 0 | 7749.9215 | 0 | 7479.3303 | 0 | 7473.6721 | 0 | 7783.5473
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 |  | 0.47 |  | 0.46 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.3 |  | 19.7 |  | 20 |  | 19.7 |  | 19.5 |  | 20.3
| LIQUID LEVEL | mm | mm |  | 191.7 |  | 125.7 |  | 210.6 |  | 205.6 |  | 158.1 |  | 192.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.55 |  | 5.48 |  | 5.52 |  | 5.69 |  | 5.42 |  | 5.23
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 12
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-12
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.4 |  | 83.2 | 72.6 | 73.8 |  | 74.6 | 79.9 | 77.4 |  | 75
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.9 |  | 80 | 69.4 | 70.5 |  | 69.2 | 76.1 | 72.3 |  | 70.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.3 |  | 67.9 | 61.5 | 65.2 |  | 66.8 | 69.1 | 72.6 |  | 70
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.8 |  | 52.2 | 38.8 | 41.4 |  | 32.4 | 57.3 | 55.4 |  | 41.1
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 114.3 |  | 116.3 | 117 | 115.9 |  | 114.2 | 120.6 | 116.4 |  | 115.8
| INPUT | Kw | 1194kW |  | 1133 |  | 1193 | 1187 | 1191 |  | 1169 | 1227 | 1194 |  | 1187
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49882 |  | 51100.9 | 48823.2 | 48812.4 |  | 51195.9 | 50379.4 | 50368.6 |  | 50472.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59.1 | 57.8 | 57.7 |  | 57.2 | 58.5 | 58.4 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.48 | 0.59 | 0.58 |  | 0.52 | 0.47 | 0.47 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 44.9 | 45 | 45 |  | 44.9 | 45 | 45.1 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.22 |  | 0.21 | 0.23 | 0.22 |  | 0.22 | 0.22 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.6 | 4.4 | 4 |  | 3.7 | 4 | 3.7 |  | 4.1
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.2 |  | 1.7 | 3.6 | 3 |  | 2.7 | 2.5 | 2.8 |  | 3
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0 | 2.6 | 1.2 | 1.3 | 0 | 1 | 1.6 | 1 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 653.44 |  | 632.32 | 678.6 | 634.88 |  | 624.64 | 685.4 | 632 |  | 631.36
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.8 |  | 12.8 | 13.3 | 13.5 |  | 13.2 | 12.7 | 12.8 |  | 12.9
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4 |  | 4.3 | 4.8 | 4.3 |  | 3.7 | 4.1 | 3.8 |  | 4.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.8 | 0 | 8.5 | 8.5 | 9.2 | 0 | 9.5 | 8.6 | 9 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6640.037 | 0 | 6206.3741 | 6660.6236 | 6744.6836 | 0 | 6852.2864 | 6806.5127 | 6568.1293 | 0 | 6342.7621
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 |  | 0.82 | 0.83 | 0.81 |  | 0.8 | 0.8 | 0.79 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.1 |  | 35.7 | 36.2 | 35.5 |  | 35.4 | 35.3 | 34.7 |  | 35.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.5 |  | 36.3 | 36.9 | 36.1 |  | 35.7 | 35.8 | 35.1 |  | 36
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.4 | 0 | 3.7 | 2.1 | 2.8 | 0 | 3 | 1.5 | 2.4 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.9 |  | 27.7 | 29.3 | 27.8 |  | 27.5 | 28.9 | 27.6 |  | 27.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.1 |  | 32.6 | 34.8 | 33.3 |  | 32.7 | 34.3 | 32.7 |  | 33.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 0 | 4.9 | 5.5 | 5.5 | 0 | 5.2 | 5.4 | 5.1 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1296.26 |  | 1301.16 | 1291.6 | 1298.5 |  | 1289.4 | 1300.46 | 1290.38 |  | 1295.28
| HEAT CAPACITY | kW | 8226.9 | 0 | 7783.5473 | 0 | 7362.2217 | 8203.0023 | 8246.8245 | 0 | 7742.3557 | 8109.1039 | 7599.2356 | 0 | 7927.2333
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.45 |  | 0.44 | 0.46 | 0.45 |  | 0.45 | 0.45 | 0.44 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.2 |  | 18.8 | 19.7 | 19 |  | 19.2 | 18.8 | 18.5 |  | 19.1
| LIQUID LEVEL | mm | mm |  | 198.8 |  | 132.5 | 200.9 | 197.4 |  | 211.5 | 155.6 | 163.7 |  | 198.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.95 |  | 5.47 | 5.39 | 5.65 |  | 5.88 | 5.35 | 5.73 |  | 5.22
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 13
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-13
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 71.7 | 71.5 |  | 83.4 |  | 74.7 | 74 | 73 |  | 75.5 |  | 75.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 66.2 | 66 |  | 80.2 |  | 69.6 | 68.7 | 67.9 |  | 71.3 |  | 70.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.4 | 65.9 |  | 67.5 |  | 64.7 | 65.8 | 65.8 |  | 71.7 |  | 68
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 37.6 | 35.9 |  | 51.6 |  | 40.9 | 33.4 | 31.9 |  | 57 |  | 41.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 116.9 | 116.3 |  | 117.6 |  | 117.3 | 115.2 | 115.1 |  | 117.5 |  | 117.3
| INPUT | Kw | 1194kW | 1152 | 1137 |  | 1191 |  | 1184 | 1173 | 1164 |  | 1188 |  | 1184
COMPRESSOR | RUNNING TIME | Hr | NA | 49899.5 | 49891.2 |  | 51110 |  | 48834.7 | 51214.1 | 51205.8 |  | 50387.4 |  | 50481.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.1 |  | 59 |  | 57.7 | 57.2 | 57.3 |  | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  | 0.58 | 0.52 | 0.52 |  | 0.57 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.2 | 45 |  | 45.1 |  | 45.1 | 45.9 | 45 |  | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.22 |  | 0.2 |  | 0.22 | 0.22 | 0.22 |  | 0.21 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.2 | 3.8 |  | 2.4 |  | 3.8 | 3.9 | 3.8 |  | 3.9 |  | 3.9
| SATURATION TEMPERATURE | CELCIUS | C | 3.5 | 3.2 |  | 4.8 |  | 3 | 2.6 | 2.8 |  | 2.2 |  | 2.8
| APPROACH TEMP | CELCIUS | C | 0.8 | 0.9 | 0 | -1.1 | 0 | 1.3 | 1 | 0.9 | 0 | 1.7 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 644.48 | 652.8 |  | 641.4 |  | 640.2 | 629.44 | 626.8 |  | 636.6 |  | 641.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.2 | 12.8 |  | 12.4 |  | 13.1 | 13 | 13.2 |  | 12.8 |  | 12.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 4.1 |  | 3.7 |  | 4.3 | 3.6 | 3.7 |  | 3.9 |  | 3.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.9 | 8.7 | 0 | 8.7 | 0 | 8.8 | 9.4 | 9.5 | 0 | 8.9 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 6623.4088 | 6558.1524 | 0 | 6443.6259 | 0 | 6505.4965 | 6832.2587 | 6875.9815 | 0 | 6542.4249 | 0 | 6374.5266
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.8 |  | 0.82 |  | 0.81 | 0.82 | 0.81 |  | 0.79 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.5 | 35.3 |  | 35.7 |  | 35.6 | 35.8 | 35.6 |  | 35 |  | 35.5
| SATURATED TEMEPRATURE | CELCIUS | C | 36 | 35.8 |  | 36.6 |  | 36.3 | 36.3 | 36 |  | 35.3 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.4 | 1.7 | 0 | 3.2 | 0 | 2.1 | 3 | 2.3 | 0 | 1.4 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.5 | 28.7 |  | 28.7 |  | 28.6 | 28.3 | 28.7 |  | 28.5 |  | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.6 | 34.1 |  | 33.4 |  | 34.2 | 33.3 | 33.7 |  | 33.9 |  | 33.8
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.1 | 5.4 | 0 | 4.7 | 0 | 5.6 | 5 | 5 | 0 | 5.4 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1302.7 | 1294 |  | 1301.5 |  | 1296.4 | 1290.94 | 1298.7 |  | 1297.2 |  | 1299.2
| HEAT CAPACITY | kW | 8226.9 | 7671.7898 | 8068.8222 | 0 | 7063.5681 | 0 | 8383.1871 | 7453.4642 | 7498.2679 | 0 | 8088.776 | 0 | 7951.224
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.45 |  | 0.44 |  | 0.45 | 0.46 | 0.45 |  | 0.44 |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C | 19.5 | 35.8 |  | 18.5 |  | 19.2 | 19.5 | 19.4 |  | 18.6 |  | 19.1
| LIQUID LEVEL | mm | mm | 198.9 | 201.8 |  | 133.3 |  | 198.8 | 216.7 | 211.9 |  | 163.8 |  | 201.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.97 | 5.8 |  | 5.59 |  | 5.61 | 5.76 | 5.84 |  | 5.62 |  | 5.2
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 14
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-14
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71 |  | 82.3 | 75.8 | 74.6 |  | 70.1 | 77 | 77 |  | 73.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.7 |  | 78.1 | 70.2 | 69.5 |  | 65.9 | 72 | 72.3 |  | 68.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.5 |  | 68.2 | 63.3 | 63.2 |  | 65.9 | 70.8 | 72.2 |  | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.8 |  | 53 | 41 | 38.3 |  | 30.6 | 58.2 | 58.1 |  | 44.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.5 |  | 118.2 | 117 | 117.4 |  | 113 | 117.7 | 118.9 |  | 118
| INPUT | Kw | 1194kW |  | 1155 |  | 1197 | 1198 | 1189 |  | 1145 | 1206 | 1208 |  | 1192
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49909.5 |  | 51119.8 | 48853.2 | 48843.9 |  | 51229.3 | 50405.8 | 50396.6 |  | 50490.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.2 | 57.6 | 57.6 |  | 57.2 | 58.6 | 58.7 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.48 | 0.59 | 0.59 |  | 0.52 | 0.47 | 0.47 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 |  | 44.9 | 45.1 | 45 |  | 45.1 | 44.9 | 44.9 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.22 | 0.22 |  | 0.22 | 0.23 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.2 |  | 3 | 4.1 | 4 |  | 3.7 | 4.1 | 4.3 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.6 |  | 2.1 | 3.3 | 3.3 |  | 2.4 | 3.2 | 3.2 |  | 3.7
| APPROACH TEMP | CELCIUS | C |  | 1 | 0 | 2.5 | 1.5 | 0.8 | 0 | 1.6 | 0.9 | 1.2 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 670.7 |  | 641.4 | 678.08 | 646.05 |  | 638.1 | 685.36 | 656 |  | 637.2
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.3 |  | 13.5 | 13.2 | 13.1 |  | 12.9 | 12.5 | 13.4 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.6 | 4.8 | 4.1 |  | 4 | 4.1 | 4.4 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.7 | 0 | 8.9 | 8.4 | 9 | 0 | 8.9 | 8.4 | 9 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6737.9792 | 0 | 6591.7552 | 6577.2194 | 6714.1455 | 0 | 6557.8406 | 6647.8337 | 6817.552 | 0 | 6475.0115
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 |  | 0.83 | 0.84 | 0.82 |  | 0.81 | 0.81 | 0.8 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.7 |  | 36.2 | 36.5 | 36 |  | 35.6 | 35.5 | 35.3 |  | 35.9
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.1 |  | 37 | 37.3 | 36.7 |  | 36.1 | 36 | 35.7 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.6 | 0 | 3.2 | 2.8 | 2.1 | 0 | 2.2 | 31.9 | 1.5 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29 |  | 29 | 29 | 29.1 |  | 28.9 | 28.7 | 28.7 |  | 28.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.5 |  | 33.8 | 34.5 | 34.6 |  | 33.9 | 4.1 | 34.2 |  | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 4.8 | 5.5 | 5.5 | 0 | 5 | -24.6 | 5.5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1298.8 |  | 1303.6 | 1288.28 | 1292.6 |  | 1299.5 | 1294.16 | 1294.9 |  | 1286.2
| HEAT CAPACITY | kW | 8226.9 | 0 | 8248.7298 | 0 | 7225.4965 | 8181.9169 | 8209.3533 | 0 | 7502.8868 | -36762.5127 | 8223.9607 | 0 | 7723.1409
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 | 0.46 | 0.46 |  | 0.46 | 0.45 | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.6 |  | 18.9 | 19.7 | 19.5 |  | 19.4 | 18.9 | 18.9 |  | 19.9
| LIQUID LEVEL | mm | mm |  | 204 |  | 124.2 | 197.3 | 205.5 |  | 209.7 | 151.7 | 154.2 |  | 198.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.57 |  | 5.45 | 5.31 | 5.61 |  | 5.76 | 5.22 | 5.5 |  | 5.43
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 15
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-15
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.1 |  | 81.9 |  | 73.8 |  | 71.3 |  | 76.4 |  | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.4 |  | 77.5 |  | 67.8 |  | 65.8 |  | 71.1 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.2 |  | 69.3 |  | 63.9 |  | 66.4 |  | 74.2 |  | 72.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 40.1 |  | 55.9 |  | 40.6 |  | 31.5 |  | 58.2 |  | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.6 |  | 118.1 |  | 115.5 |  | 113.3 |  | 118.8 |  | 118.6
| INPUT | Kw | 1194kW |  | 1145 |  | 1194 |  | 1180 |  | 1144 |  | 1202 |  | 1197
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49919.3 |  | 51129.9 |  | 48862.4 |  | 51239.3 |  | 50419.6 |  | 50500.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.8 |  | 59.2 |  | 57.9 |  | 57.2 |  | 58.6 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.48 |  | 0.59 |  | 0.52 |  | 0.47 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 44.9 |  | 44.9 |  | 45.1 |  | 44.8 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 |  | 0.22 |  | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.1 |  | 4.4 |  | 3.7 |  | 4.4 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.7 |  | 2.2 |  | 3.4 |  | 2.6 |  | 3.2 |  | 3.6
| APPROACH TEMP | CELCIUS | C |  | 1.1 | 0 | 2.6 | 0 | 0.7 | 0 | 1.3 | 0 | 1.4 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 662.4 |  | 640.6 |  | 639.6 |  | 637.8 |  | 647.5 |  | 640
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.7 |  | 13.8 |  | 13.2 |  | 13.1 |  | 13.8 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 |  | 4.8 |  | 4.1 |  | 3.9 |  | 4.6 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.9 | 0 | 9 | 0 | 9.1 | 0 | 9.2 | 0 | 9.2 | 0 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6807.5751 | 0 | 6657.5058 | 0 | 6720.97 | 0 | 6775.7044 | 0 | 6878.7529 | 0 | 6577.3672
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 |  | 0.82 |  | 0.81 |  | 0.8 |  | 0.8 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.3 |  | 35.9 |  | 35.6 |  | 35.4 |  | 34.9 |  | 35.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.7 |  | 36.7 |  | 36.3 |  | 35.8 |  | 35.4 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.6 | 0 | 3.2 | 0 | 2.2 | 0 | 2.3 | 0 | 1.5 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.6 |  | 28.5 |  | 28.7 |  | 28.6 |  | 28.3 |  | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.1 |  | 33.5 |  | 34.1 |  | 33.5 |  | 33.9 |  | 33.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 5 | 0 | 5.4 | 0 | 4.9 | 0 | 5.6 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1293.6 |  | 1302.6 |  | 1289.9 |  | 1296.9 |  | 1290.8 |  | 1296.4
| HEAT CAPACITY | kW | 8226.9 | 0 | 8215.7044 | 0 | 7520.7852 | 0 | 8043.2564 | 0 | 7338.1178 | 0 | 8346.9746 | 0 | 7934.0878
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 |  | 0.46 |  | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.6 |  | 18.7 |  | 19.5 |  | 19.4 |  | 18.9 |  | 19.6
| LIQUID LEVEL | mm | mm |  | 193.4 |  | 123.2 |  | 206.6 |  | 202.5 |  | 158.5 |  | 198
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.73 |  | 5.55 |  | 5.71 |  | 5.93 |  | 5.62 |  | 5.43
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 16
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-16
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.4 |  | 81.3 | 75.2 | 72 |  | 70.4 | 75.8 | 78.5 |  | 74.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.4 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.3 |  | 77.1 | 70.7 | 68.2 |  | 65 | 70.4 | 74.1 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.5 |  | 70.4 | 63.8 | 64.7 |  | 66.5 | 72.7 | 74.8 |  | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 42 |  | 56 | 38.8 | 42.1 |  | 34.9 | 52.1 | 58.2 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.9 |  | 116.7 | 118 | 114.6 |  | 111.9 | 117.6 | 118.9 |  | 116.8
| INPUT | Kw | 1194kW |  | 1125 |  | 1175 | 1209 | 1153 |  | 1133 | 1207 | 1200 |  | 1179
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49937.5 |  | 51140 | 48881.1 | 48872.4 |  | 51261 | 50438.2 | 50429.6 |  | 50510.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 |  | 58.9 | 58 | 57.7 |  | 57.2 | 58.7 | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.48 | 0.59 | 0.58 |  | 0.52 | 0.48 | 0.57 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 |  | 45 | 44.9 | 45.1 |  | 45 | 44.9 | 45 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.21 |  | 0.21 | 0.23 | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 3.9 |  | 2.8 | 4.5 | 4 |  | 3.9 | 4.5 | 4 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.3 |  | 2 | 3.7 | 3.2 |  | 2.4 | 3.2 | 2.8 |  | 3.1
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | 2.6 | 0.8 | 1.4 | 0 | 1.3 | 1.4 | 1.3 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 656.4 |  | 635.6 | 679.82 | 637.4 |  | 624.8 | 686.7 | 642.3 |  | 638.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.3 |  | 13.4 | 13.2 | 13.5 |  | 13 | 13.2 | 13.4 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.3 |  | 4.6 | 4.5 | 4.6 |  | 3.7 | 4.6 | 4.1 |  | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9 | 0 | 8.8 | 8.7 | 8.9 | 0 | 9.3 | 8.6 | 9.3 | 0 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6821.709 | 0 | 6458.7529 | 6829.6005 | 6550.6467 | 0 | 6709.746 | 6819.4226 | 6897.679 | 0 | 6566.0624
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.78 |  | 0.8 | 0.84 | 0.8 |  | 0.78 | 0.81 | 0.77 |  | 0.79
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 34.5 |  | 35 | 36.7 | 34.8 |  | 34.7 | 35.9 | 34.1 |  | 34.7
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.1 |  | 36 | 37.5 | 35.6 |  | 35.1 | 36.2 | 34.7 |  | 35.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.7 | 1 | 3.3 | 2.1 | 2.2 | 0 | 2.3 | 1.5 | 1.6 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.9 |  | 27.8 | 29.8 | 27.2 |  | 27.8 | 29.3 | 27.5 |  | 27.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.4 |  | 32.7 | 35.4 | 33.4 |  | 32.8 | 34.7 | 33.1 |  | 33
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 4.9 | 5.6 | 6.2 | 0 | 5 | 5.4 | 5.6 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1295.8 |  | 1300.6 | 1297.8 | 1295.8 |  | 1293.1 | 1299.6 | 1285.4 |  | 1296.4
| HEAT CAPACITY | kW | 8226.9 | 0 | 8229.6767 | 0 | 7359.0531 | 8392.2402 | 9277.0901 | 0 | 7465.9353 | 8103.7413 | 8312.0554 | 0 | 8083.7875
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.45 |  | 0.44 | 0.47 | 0.45 |  | 0.45 | 0.46 | 0.44 |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C |  | 18.9 |  | 18.2 | 20 | 19 |  | 19.1 | 19.4 | 18.1 |  | 18.9
| LIQUID LEVEL | mm | mm |  | 201.7 |  | 117.8 | 212.1 | 200.8 |  | 206.4 | 157.3 | 160 |  | 199.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 6.04 |  | 5.72 | 5.33 | 5.9 |  | 6 | 5.25 | 5.68 |  | 5.33
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 17
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-17
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  |  |  |  | 74 |  |  |  | 80.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  |  |  |  | 0 |  |  |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  |  |  |  | 71.7 |  |  |  | 75.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  |  |  |  | 63.9 |  |  |  | 75.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  |  |  |  | 38.5 |  |  |  | 56.1
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  |  |  |  | 6.6 |  |  |  | 6.6
| CURRENT | A | ≤115A |  |  |  |  | 117 |  |  |  | 120.2
| INPUT | Kw | 1194kW |  |  |  |  | 1196 |  |  |  | 1227
COMPRESSOR | RUNNING TIME | Hr | NA |  |  |  |  | 48899.8 |  |  |  | 50460.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  |  |  |  | 57.9 |  |  |  | 58.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  |  |  |  | 0.59 |  |  |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  |  |  |  | 45 |  |  |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  |  |  |  | 0.23 |  |  |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  |  |  |  | 4.1 |  |  |  | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  |  |  |  | 3.2 |  |  |  | 3.2
| APPROACH TEMP | CELCIUS | C | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  |  |  |  | 687.9 |  |  |  | 685.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  |  |  |  | 13.1 |  |  |  | 13.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  |  |  |  | 4 |  |  |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 0 | 0 | 0 | 9.1 | 0 | 0 | 0 | 9 | 0 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 0 | 0 | 0 | 7228.5104 | 0 | 0 | 0 | 7123.0947 | 0 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  |  |  |  | 0.82 |  |  |  | 0.8
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  |  |  |  | 35.8 |  |  |  | 34.9
| SATURATED TEMEPRATURE | CELCIUS | C |  |  |  |  | 36.6 |  |  |  | 35.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  |  |  |  | 28.9 |  |  |  | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  |  |  |  | 34.4 |  |  |  | 34
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 0 | 0 | 0 | 5.5 | 0 | 0 | 0 | 5.5 | 0 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  |  |  |  | 1297.9 |  |  |  | 1309.7
| HEAT CAPACITY | kW | 8226.9 | 0 | 0 | 0 | 0 | 8243.0139 | 0 | 0 | 0 | 8317.9561 | 0 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  |  |  |  | 0.45 |  |  |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C |  |  |  |  | 19.2 |  |  |  | 19
| LIQUID LEVEL | mm | mm |  |  |  |  | 204.3 |  |  |  | 163.4
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  |  |  |  | 5.6 |  |  |  | 5.42
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 18
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-18
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 72.2 | 71 |  | 80.8 |  | 74.6 | 72.3 | 71.7 |  | 76.6 |  | 72.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.5 |  | 0 |  | 0 | 0.1 | 0 |  | 0.2 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 67 | 65.2 |  | 76.1 |  | 70.2 | 69.6 | 69.2 |  | 71.6 |  | 66.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 68.8 | 67.5 |  | 68.8 |  | 64.8 | 66.1 | 65.8 |  | 72.1 |  | 74
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 40.8 | 37.9 |  | 53.1 |  | 37.4 | 34.6 | 33.4 |  | 56.1 |  | 44.1
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118.4 | 117.8 |  | 117.8 |  | 116.9 | 114.2 | 113.2 |  | 119.1 |  | 117.2
| INPUT | Kw | 1194kW | 1166 | 1142 |  | 1186 |  | 1182 | 1166 | 1144 |  | 1200 |  | 1178
COMPRESSOR | RUNNING TIME | Hr | NA | 49966.9 | 49955.7 |  | 51157.8 |  | 48911.8 | 51290.7 | 51279.5 |  | 50467.4 |  | 50528.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.8 | 58.6 |  | 59.2 |  | 57.9 | 57.2 | 57.2 |  | 58.8 |  | 59.8
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 |  | 0.49 |  | 0.58 | 0.52 | 0.52 |  | 0.47 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 44.9 |  | 45 |  | 45 | 45 | 45.1 |  | 44.9 |  | 45.3
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.21 |  | 0.22 | 0.22 | 0.21 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.4 | 4.3 |  | 3.2 |  | 4 | 3.5 | 3.5 |  | 4.3 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C | 4 | 3.8 |  | 2.4 |  | 3.2 | 2.5 | 2.4 |  | 3.2 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 1 | 1 | 0 | 2.3 | 0 | 0.8 | 1.3 | 1.2 | 0 | 1.3 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 667.7 | 678.9 |  | 656.8 |  | 636.2 | 632.5 | 636.1 |  | 663.2 |  | 651.5
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 14 | 13.4 |  | 13.4 |  | 13.1 | 13 | 12.7 |  | 13.3 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5 | 4.8 |  | 4.7 |  | 4 | 3.8 | 3.6 |  | 4.5 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9 | 8.6 | 0 | 8.7 | 0 | 9.1 | 9.2 | 9.1 | 0 | 8.8 | 0 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW | 6939.1455 | 6741.963 | 0 | 6598.3372 | 0 | 6685.2425 | 6719.3995 | 6684.1917 | 0 | 6739.2148 | 0 | 6319.3995
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.81 |  | 0.83 |  | 0.82 | 0.81 | 0.81 |  | 0.81 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.7 | 35.6 |  | 36.1 |  | 35.9 | 35.8 | 35.8 |  | 35.1 |  | 35.7
| SATURATED TEMEPRATURE | CELCIUS | C | 36.2 | 36.1 |  | 37 |  | 36.6 | 36.3 | 36.1 |  | 35.7 |  | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 1.6 | 1 | 3.2 | 0 | 2.1 | 2.3 | 2.2 | 0 | 1.5 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29 | 28 |  | 28.9 |  | 29.1 | 29 | 29 |  | 28.7 |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.5 | 34.5 |  | 33.8 |  | 34.5 | 34 | 33.9 |  | 34.2 |  | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 6.5 | 0 | 4.9 | 0 | 5.4 | 5 | 4.9 | 0 | 5.5 | 0 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1292.1 | 1299.3 |  | 1301.9 |  | 1298.3 | 1306 | 1299.7 |  | 1288.5 |  | 1301.1
| HEAT CAPACITY | kW | 8226.9 | 8206.1778 | 9752.2517 | 0 | 7366.4088 | 0 | 8095.6351 | 7540.4157 | 7353.9607 | 0 | 8183.3141 | 0 | 8263.3372
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.46 |  | 0.45 |  | 0.46 | 0.45 | 0.45 |  | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.8 | 19.7 |  | 19 |  | 19.4 | 19.3 | 19.2 |  | 18.9 |  | 20.1
| LIQUID LEVEL | mm | mm | 205.5 | 209.9 |  | 122.5 |  | 204 | 206 | 206.9 |  | 161.8 |  | 199.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.72 | 5.59 |  | 5.45 |  | 5.7 | 5.78 | 5.93 |  | 5.42 |  | 5.28
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 19
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-19
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.1 |  | 79.5 |  | 74.6 |  | 75.6 |  | 77.1 |  | 74.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 |  | 0 |  | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.4 |  | 76 |  | 70.1 |  | 70.8 |  | 72.7 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.8 |  | 70.3 |  | 63.6 |  | 65.9 |  | 74.7 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.8 |  | 53.1 |  | 38.5 |  | 34.6 |  | 63.3 |  | 45
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116 |  | 117.8 |  | 116.5 |  | 116.8 |  | 119.7 |  | 118
| INPUT | Kw | 1194kW |  | 1142 |  | 1186 |  | 1187 |  | 1185 |  | 1209 |  | 1192
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49976.1 |  | 51167.5 |  | 48921.6 |  | 51301.5 |  | 50477.2 |  | 50537.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.6 |  | 59.2 |  | 57.7 |  | 57.5 |  | 58.7 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 |  | 0.45 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.3 |  | 44.9 |  | 44.3 |  | 44.6 |  | 44.9 |  | 45.2
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.24 |  | 0.22 |  | 0.23 |  | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.5 |  | 3.4 |  | 4.4 |  | 3.7 |  | 4.2 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 |  | 2.4 |  | 3.4 |  | 2.9 |  | 3.1 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0 | 0.7 | 0 | 2.2 | 0 | 1.2 | 0 | 1 | 0 | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 640.88 |  | 647.52 |  | 637.28 |  | 642.64 |  | 631.44 |  | 646.32
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.4 |  | 13.7 |  | 12.9 |  | 13.5 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.6 |  | 4.6 |  | 3.9 |  | 4.2 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.9 | 0 | 8.8 | 0 | 9.1 | 0 | 9 | 0 | 9.3 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6586.4111 | 0 | 6579.8799 | 0 | 6696.5912 | 0 | 6678.7067 | 0 | 6781.0531 | 0 | 6493.0531
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 |  | 0.83 |  | 0.83 |  | 0.81 |  | 0.8 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.6 |  | 36.1 |  | 35.9 |  | 35.8 |  | 35.2 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.1 |  | 37 |  | 36.7 |  | 36.2 |  | 35.8 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.5 | 1 | 3.7 | 0 | 2.9 | 0 | 2.9 | 0 | 2.4 | 0 | 2.7
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.5 |  | 28.4 |  | 28.3 |  | 28.2 |  | 28.3 |  | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.6 |  | 33.3 |  | 33.8 |  | 33.3 |  | 33.4 |  | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 0 | 4.9 | 0 | 5.5 | 0 | 5.1 | 0 | 5.1 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1296.82 |  | 1302.56 |  | 1296.54 |  | 1296.12 |  | 1285.34 |  | 1297.94
| HEAT CAPACITY | kW | 8226.9 | 0 | 7637.1617 | 0 | 7370.1432 | 0 | 8234.3764 | 0 | 7633.0393 | 0 | 7569.5543 | 0 | 8093.3903
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.45 |  | 0.46 |  | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.8 |  | 19.3 |  | 19.6 |  | 19.4 |  | 19.1 |  | 19.8
| LIQUID LEVEL | mm | mm |  | 201.8 |  | 117.7 |  | 209 |  | 221 |  | 161.8 |  | 194.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.91 |  | 5.52 |  | 5.78 |  | 5.68 |  | 5.76 |  | 5.54
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 20
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-20
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70 |  | 77.7 | 74 | 73.5 |  | 71.7 | 76.4 | 75.6 |  | 74
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.3 |  | 73.1 | 70.7 | 68.2 |  | 68.9 | 71.6 | 71 |  | 68.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66 |  | 68.4 | 64.3 | 63.9 |  | 65.2 | 72.8 | 72 |  | 72.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 35.4 |  | 49 | 38.8 | 36.7 |  | 31.5 | 56.5 | 42.3 |  | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.9 |  | 114.7 | 117.2 | 115.4 |  | 113.9 | 116.3 | 118 |  | 117.4
| INPUT | Kw | 1194kW |  | 1155 |  | 1175 | 1206 | 1194 |  | 1172 | 1198 | 1205 |  | 1201
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50000.8 |  | 51177.9 | 48951.8 | 48941.1 |  | 51311.9 | 50498.2 | 50487.5 |  | 50547.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.6 |  | 59 | 57.8 | 58 |  | 57.6 | 58.4 | 58.7 |  | 59.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 | 0.59 | 0.59 |  | 0.52 | 0.47 | 0.53 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.7 |  | 45.1 | 45 | 45 |  | 44.8 | 45.1 | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.23 | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.6 | 4.5 | 4.4 |  | 4 | 4.3 | 4.2 |  | 4.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.5 | 3.6 | 3.5 |  | 2.8 | 3.3 | 3.2 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0 | 2.3 | 0.8 | 1.1 | 0 | 0.7 | 1.1 | 1.2 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 667.28 |  | 644.72 | 679.4 | 638.08 |  | 630.66 | 686.7 | 648.8 |  | 646.16
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.5 | 13.2 | 13.5 |  | 12.8 | 13.3 | 13.5 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.8 | 4.4 | 4.6 |  | 3.5 | 4.4 | 4.4 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.9 | 0 | 8.7 | 8.8 | 8.9 | 0 | 9.3 | 8.9 | 9.1 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6857.7275 | 0 | 6476.9792 | 6903.8337 | 6557.6351 | 0 | 6772.6767 | 7057.3095 | 6817.6443 | 0 | 6491.4457
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.84 | 0.82 | 0.83 |  | 0.82 | 0.79 | 0.8 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 |  | 36.6 | 35.7 | 36.6 |  | 36.6 | 34.8 | 35.9 |  | 36.7
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 37.1 | 36.4 | 36.8 |  | 36.3 | 35.3 | 35.8 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.4 | 0 | 3.7 | 2.1 | 2.8 | 0 | 3 | 1.6 | 2.4 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.7 |  | 28.5 | 28.7 | 28.6 |  | 28.3 | 28.3 | 28.4 |  | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34 |  | 33.4 | 34.3 | 34 |  | 33.3 | 33.7 | 33.4 |  | 34
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 0 | 4.9 | 5.6 | 5.4 | 0 | 5 | 5.4 | 5 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1298.78 |  | 1302 | 1302.5 | 1298.92 |  | 1296.38 | 1288.7 | 1294.44 |  | 1297.94
| HEAT CAPACITY | kW | 8226.9 | 0 | 7948.6536 | 0 | 7366.9746 | 8422.6328 | 8099.5012 | 0 | 7484.873 | 8035.7737 | 7473.6721 | 0 | 7943.5127
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.46 | 0.47 |  | 0.46 | 0.45 | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.3 |  | 19.7 | 19.3 | 20 |  | 19.7 | 18.9 | 19.5 |  | 20.3
| LIQUID LEVEL | mm | mm |  | 191.7 |  | 125.7 | 214.5 | 210.6 |  | 205.6 | 163.3 | 158.1 |  | 192.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.55 |  | 5.48 | 5.37 | 5.52 |  | 5.69 | 5.46 | 5.42 |  | 5.23
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 21
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-21
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.6 | 69.3 |  | 78.7 |  | 73.8 | 71.1 | 71.3 |  | 74.9 |  | 72.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.9 | 62.8 |  | 74.2 |  | 68 | 68.1 | 68.3 |  | 70.7 |  | 66.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.4 | 69.2 |  | 70.7 |  | 64.1 | 66.4 | 65.8 |  | 75.4 |  | 72.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 38.1 | 39 |  | 50.8 |  | 40.1 | 31.7 | 34.2 |  | 52.8 |  | 40.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 117.1 | 117 |  | 116.4 |  | 118 | 112.2 | 115.9 |  | 119.4 |  | 117.7
| INPUT | Kw | 1194kW | 1161 | 1145 |  | 1177 |  | 1200 | 1150 | 1173 |  | 1205 |  | 1187
COMPRESSOR | RUNNING TIME | Hr | NA | 50019 | 50010.3 |  | 51187.6 |  | 48959.9 | 51330.4 | 51321.8 |  | 50508.1 |  | 50557
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.2 |  | 59.2 |  | 57.7 | 57.2 | 57.3 |  | 58.7 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 44.9 |  | 45 |  | 45 | 45 | 45.1 |  | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.21 |  | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4 | 4.4 |  | 3.1 |  | 4.4 | 3.7 | 3.9 |  | 4.4 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C | 3.4 | 3.9 |  | 2.3 |  | 3.5 | 2.9 | 2.9 |  | 3.3 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0.9 | 0.9 | 0 | 2.5 | 0 | 0.7 | 1.1 | 1.2 | 0 | 1.2 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 633.04 | 659.4 |  | 640.5 |  | 646.8 | 641.2 | 629.9 |  | 642 |  | 643.3
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.6 | 13.6 |  | 13.6 |  | 13.2 | 13.2 | 13.3 |  | 13.7 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 4.8 |  | 4.8 |  | 4.2 | 4 | 4.1 |  | 4.5 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9.3 | 8.8 | 0 | 8.8 | 0 | 9 | 9.2 | 9.2 | 0 | 9.2 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 6798.2356 | 6700.6005 | 0 | 6508.545 | 0 | 6721.94 | 6811.8245 | 6691.7783 | 0 | 6820.3233 | 0 | 6462.7136
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.82 |  | 0.84 |  | 0.83 | 0.81 | 0.82 |  | 0.82 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.3 | 35.9 |  | 36.3 |  | 36.3 | 35.5 | 36.2 |  | 35.7 |  | 36.1
| SATURATED TEMEPRATURE | CELCIUS | C | 36 | 36.4 |  | 37.3 |  | 37 | 36.1 | 36.6 |  | 36 |  | 36.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.5 | 1.6 | 0 | 3.2 | 0 | 2.1 | 3 | 2.2 | 0 | 1.5 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.3 | 29.4 |  | 29.3 |  | 29.5 | 28 | 29.4 |  | 29.1 |  | 29.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.5 | 34.8 |  | 34.1 |  | 34.9 | 33.1 | 34.4 |  | 34.5 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.2 | 5.4 | 0 | 4.8 | 0 | 5.4 | 5.1 | 5 | 0 | 5.4 | 0 | 5.1
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1296.4 | 1304.5 |  | 1295.3 |  | 1292.9 | 1293.74 | 1298.6 |  | 1298.5 |  | 1297
| HEAT CAPACITY | kW | 8226.9 | 7784.388 | 8134.2956 | 0 | 7179.4919 | 0 | 8061.963 | 7619.0231 | 7497.6905 | 0 | 8096.8822 | 0 | 7638.2217
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.47 |  | 0.46 |  | 0.46 | 0.45 | 0.46 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.1 | 20.1 |  | 19.8 |  | 19.8 | 19.5 | 19.7 |  | 19.2 |  | 20.2
| LIQUID LEVEL | mm | mm | 203.8 | 197.2 |  | 128.1 |  | 204.5 | 209.6 | 203.3 |  | 158.8 |  | 196.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.9 | 5.68 |  | 5.58 |  | 5.57 | 5.71 | 5.63 |  | 5.59 |  | 5.24
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 22
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-22
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 68.7 |  | 81.4 |  | 74 |  | 71.1 |  | 75.8 |  | 74.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 63 |  | 77.5 |  | 68.5 |  | 65 |  | 71 |  | 69.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.4 |  | 70.4 |  | 64.3 |  | 65.8 |  | 75.1 |  | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 41.3 |  | 56.4 |  | 41.5 |  | 32.3 |  | 40 |  | 46
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.6 |  | 117.9 |  | 116.7 |  | 113.6 |  | 118.9 |  | 118.8
| INPUT | Kw | 1194kW |  | 1119 |  | 1186 |  | 1174 |  | 1146 |  | 1195 |  | 1195
COMPRESSOR | RUNNING TIME | Hr | NA |  | 20028 |  | 51197.3 |  | 48969.5 |  | 51345.8 |  | 50517.7 |  | 50566
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 58.9 |  | 57.7 |  | 57.2 |  | 58.5 |  | 59
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 |  | 0.59 |  | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 45 |  | 45 |  | 45.1 |  | 45.1 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 |  | 0.22 |  | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3 |  | 4.1 |  | 3.8 |  | 4.3 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.1 |  | 3.4 |  | 2.9 |  | 3.1 |  | 3.6
| APPROACH TEMP | CELCIUS | C |  | 0.8 | 0 | 2.7 | 0 | 0.7 | 0 | 1.2 | 0 | 1.4 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 669 |  | 650.6 |  | 644.87 |  | 629.9 |  | 642 |  | 642.8
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.7 |  | 13.7 |  | 13.3 |  | 13 |  | 13.7 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.8 |  | 4.1 |  | 4.1 |  | 4.5 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.1 | 0 | 8.9 | 0 | 9.2 | 0 | 8.9 | 0 | 9.2 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 7029.9076 | 0 | 6686.3048 | 0 | 6850.8129 | 0 | 6473.5681 | 0 | 6820.3233 | 0 | 6457.6905
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.79 |  | 0.82 |  | 0.81 |  | 0.8 |  | 0.82 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35 |  | 35.5 |  | 35.4 |  | 35.1 |  | 35.7 |  | 35.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.5 |  | 36.5 |  | 36.1 |  | 35.6 |  | 36 |  | 36.1
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.7 | 0 | 3.3 | 0 | 2.2 | 0 | 2.2 | 0 | 1.5 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.5 |  | 28.3 |  | 28.4 |  | 28.2 |  | 29.1 |  | 28.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.8 |  | 33.2 |  | 33.9 |  | 33.4 |  | 34.5 |  | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 0 | 4.9 | 0 | 5.5 | 0 | 5.2 | 0 | 5.4 | 0 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1297.6 |  | 1298.2 |  | 1295.9 | 1293.74 | 1298.6 |  | 1294.4 |  | 1298.4
| HEAT CAPACITY | kW | 8226.9 | 0 | 7941.4319 | 0 | 7345.4734 | 0 | 8230.3118 | 0 | 7797.5982 | 0 | 8071.3164 | 0 | 8246.1894
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.44 |  | 0.46 |  | 0.46 |  | 0.46 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.5 |  | 18.6 |  | 19.3 |  | 19.6 |  | 19.2 |  | 19.4
| LIQUID LEVEL | mm | mm |  | 196.2 |  | 122.2 |  | 207.9 |  | 206.5 |  | 160.5 |  | 204.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.9 |  | 5.59 |  | 5.78 |  | 5.7 |  | 5.69 |  | 5.35
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 23
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-23
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 77.4 | 66.9 |  | 77.9 |  | 72.7 | 68.6 | 71.3 |  | 74 |  | 73.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.8 | 0.8 |  | 0 |  | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 72.2 | 59.8 |  | 75.3 |  | 67.6 | 64 | 68.1 |  | 68.1 |  | 67.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 67.6 | 70.3 |  | 70.4 |  | 63.9 | 67 | 65.2 |  | 74.5 |  | 73.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 42 | 34.8 |  | 50.5 |  | 37.1 | 33.4 | 33.4 |  | 53.5 |  | 42
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 66.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 119.1 | 114.4 |  | 116.4 |  | 116.1 | 108.8 | 114.2 |  | 117 |  | 117.9
| INPUT | Kw | 1194kW | 1174 | 1130 |  | 1182 |  | 1172 | 1115 | 1161 |  | 1190 |  | 1200
COMPRESSOR | RUNNING TIME | Hr | NA | 50046.3 | 50036.6 |  | 51206 |  | 48984.5 | 51364.4 | 51354.7 |  | 50535.6 |  | 50575.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 59.6 |  | 59.3 |  | 57.7 | 57.2 | 57.4 |  | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 45.8 |  | 45.1 |  | 45 | 45.1 | 45.1 |  | 45 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.23 |  | 0.22 |  | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.9 | 4.6 |  | 3.3 |  | 4.1 | 3.7 | 3.6 |  | 4.3 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C | 3.3 | 4 |  | 2.5 |  | 3.3 | 2.6 | 2.7 |  | 3.2 |  | 3.7
| APPROACH TEMP | CELCIUS | C |  | 1 | 0 | 2.2 | 0 | 0.8 | 1.2 | 1.2 | 0 | 1.3 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 697.6 | 639.3 |  | 645.8 |  | 640.9 | 624.9 | 630.8 |  | 653.3 |  | 638.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13 | 13.9 |  | 13.6 |  | 13 | 13.2 | 12.9 |  | 13.7 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.4 | 5 |  | 4.7 |  | 4.1 | 3.8 | 3.9 |  | 4.5 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.6 | 8.9 | 0 | 8.9 | 0 | 8.9 | 9.4 | 9 | 0 | 9.2 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 6927.6674 | 6570.1732 | 0 | 6636.9746 | 0 | 6586.6166 | 6782.9792 | 6555.6582 | 0 | 6940.3695 | 0 | 6344.7344
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.73 | 0.82 |  | 0.84 |  | 0.83 | 0.82 | 0.82 |  | 0.81 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.5 | 36 |  | 36.4 |  | 36.3 | 34.6 | 36.1 |  | 35.6 |  | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C | 35.1 | 36.4 |  | 37.4 |  | 37 | 35 | 36.6 |  | 36 |  | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 1.6 | 0 | 3.3 | 0 | 2.1 | 2.2 | 2.2 | 0 | 1.5 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.7 | 29.5 |  | 29.4 |  | 29.5 | 27.7 | 29.4 |  | 29.3 |  | 29.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.4 | 34.8 |  | 34.1 |  | 34.9 | 32.8 | 34.4 |  | 34.5 |  | 34.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.3 | 0 | 4.7 | 0 | 5.4 | 5.1 | 5 | 0 | 5.2 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1290.3 | 1302.1 |  | 1304.3 |  | 1299.4 | 1291.6 | 1298.2 |  | 1294.1 |  | 1296.3
| HEAT CAPACITY | kW | 8226.9 | 0 | 7968.9723 | 0 | 7078.7644 | 0 | 8102.4942 | 7606.4203 | 7495.3811 | 0 | 7770.5774 | 0 | 7933.4758
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.47 |  | 0.46 |  | 0.47 | 0.45 | 0.46 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 18.9 | 20.4 |  | 19.4 |  | 19.8 | 18.8 | 19.6 |  | 19.4 |  | 20.1
| LIQUID LEVEL | mm | mm | 191.1 | 200.9 |  | 109.2 |  | 200.8 | 213.9 | 196.5 |  | 160.4 |  | 192.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.67 | 5.82 |  | 5.52 |  | 5.63 | 5.87 | 5.66 |  | 5.66 |  | 5.22
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 24
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-24
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 71 | 71.4 |  | 81.3 |  | 72 | 75.6 | 70.4 |  | 78.5 |  | 74.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.4 |  | 0 |  | 0 | 0 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 67.8 | 66.3 |  | 77.1 |  | 68.2 | 71.9 | 65 |  | 74.1 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 67.6 | 69.5 |  | 70.4 |  | 64.7 | 72.7 | 66.5 |  | 74.8 |  | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 40 | 42 |  | 56 |  | 42.1 | 56.5 | 34.9 |  | 58.2 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118.8 | 115.9 |  | 116.7 |  | 114.6 | 119.36 | 111.9 |  | 118.9 |  | 116.8
| INPUT | Kw | 1194kW | 1164 | 1125 |  | 1175 |  | 1153 | 1207 | 1133 |  | 1200 |  | 1179
COMPRESSOR | RUNNING TIME | Hr | NA | 50068.3 | 50056 |  | 51216 |  | 48995 | 50556.3 | 51379 |  | 50545.6 |  | 50585.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.4 | 58 |  | 58.9 |  | 57.7 | 58.5 | 57.2 |  | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 |  | 0.48 |  | 0.58 | 0.48 | 0.52 |  | 0.57 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.8 | 45 |  | 45 |  | 45.1 | 45.6 | 45 |  | 45 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.21 |  | 0.21 |  | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.4 | 3.9 |  | 2.8 |  | 4 | 4.5 | 3.9 |  | 4 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C | 3.8 | 3.3 |  | 2 |  | 3.2 | 3.7 | 2.4 |  | 2.8 |  | 3.1
| APPROACH TEMP | CELCIUS | C | 1.2 | 1 | 0 | 2.6 | 0 | 1.4 | 1.1 | 1.3 | 0 | 1.3 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 697.1 | 656.4 |  | 635.6 |  | 637.4 | 685.6 | 624.8 |  | 642.3 |  | 638.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.5 | 13.3 |  | 13.4 |  | 13.5 | 13.6 | 13 |  | 13.4 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5 | 4.3 |  | 4.6 |  | 4.6 | 4.8 | 3.7 |  | 4.1 |  | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.5 | 9 | 0 | 8.8 | 0 | 8.9 | 8.8 | 9.3 | 0 | 9.3 | 0 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW | 6842.2055 | 6821.709 | 0 | 6458.7529 | 0 | 6550.6467 | 6966.836 | 6709.746 | 0 | 6897.679 | 0 | 6566.0624
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.78 |  | 0.8 |  | 0.8 | 0.79 | 0.78 |  | 0.77 |  | 0.79
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.4 | 34.5 |  | 35 |  | 34.8 | 34.9 | 34.7 |  | 34.1 |  | 34.7
| SATURATED TEMEPRATURE | CELCIUS | C | 35.9 | 35.1 |  | 36 |  | 35.6 | 35.5 | 35.1 |  | 34.7 |  | 35.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.6 | 1.7 | 1 | 3.3 | 0 | 2.2 | 1.6 | 2.3 | 0 | 1.6 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.6 | 27.9 |  | 27.8 |  | 27.2 | 28.5 | 27.8 |  | 27.5 |  | 27.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.3 | 33.4 |  | 32.7 |  | 33.4 | 33.9 | 32.8 |  | 33.1 |  | 33
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.7 | 5.5 | 0 | 4.9 | 0 | 6.2 | 5.4 | 5 | 0 | 5.6 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1297.6 | 1295.8 |  | 1300.6 |  | 1295.8 | 1296.5 | 1293.1 |  | 1285.4 |  | 1296.4
| HEAT CAPACITY | kW | 8226.9 | 8540.7852 | 8229.6767 | 0 | 7359.0531 | 0 | 9277.0901 | 8084.4111 | 7465.9353 | 0 | 8312.0554 | 0 | 8083.7875
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.45 |  | 0.44 |  | 0.45 | 0.45 | 0.45 |  | 0.44 |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C | 19.5 | 18.9 |  | 18.2 |  | 19 | 18.9 | 19.1 |  | 18.1 |  | 18.9
| LIQUID LEVEL | mm | mm | 206.7 | 201.7 |  | 117.8 |  | 200.8 | 157.1 | 206.4 |  | 160 |  | 199.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.46 | 6.04 |  | 5.72 |  | 5.9 | 5.41 | 6 |  | 5.68 |  | 5.33
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 25
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-25
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.1 |  | 81.9 | 75.5 | 73.8 |  | 71.3 | 71.3 | 76.4 |  | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.4 |  | 77.5 | 71.2 | 67.8 |  | 65.8 | 65.6 | 71.1 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.2 |  | 69.3 | 63.5 | 63.9 |  | 66.4 | 75 | 74.2 |  | 72.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 40.1 |  | 55.9 | 37.9 | 40.6 |  | 31.5 | 52.8 | 58.2 |  | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.6 |  | 118.1 | 118 | 115.5 |  | 113.3 | 115.2 | 118.8 |  | 118.6
| INPUT | Kw | 1194kW |  | 1145 |  | 1194 | 1212 | 1180 |  | 1144 | 1174 | 1202 |  | 1197
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50061 |  | 51223 | 49015.2 | 49008 |  | 51387 | 50576.9 | 50568.7 |  | 50594.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.8 |  | 59.2 | 57.9 | 57.9 |  | 57.2 | 58.7 | 58.6 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.48 | 0.59 | 0.59 |  | 0.52 | 0.48 | 0.47 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 44.9 | 45 | 44.9 |  | 45.1 | 45.1 | 44.8 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.23 | 0.22 |  | 0.22 | 0.23 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.1 | 4.4 | 4.4 |  | 3.7 | 4.5 | 4.4 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.7 |  | 2.2 | 3.4 | 3.4 |  | 2.6 | 3.6 | 3.2 |  | 3.6
| APPROACH TEMP | CELCIUS | C |  | 1.1 | 0 | 2.6 | 0.7 | 0.7 | 0 | 1.3 | 1.1 | 1.4 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 662.4 |  | 640.6 | 639.9 | 639.6 |  | 637.8 | 619.4 | 647.5 |  | 640
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.7 |  | 13.8 | 13.2 | 13.2 |  | 13.1 | 14 | 13.8 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 |  | 4.8 | 4.1 | 4.1 |  | 3.9 | 4.7 | 4.6 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.9 | 0 | 9 | 9.1 | 9.1 | 0 | 9.2 | 9.3 | 9.2 | 0 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6807.5751 | 0 | 6657.5058 | 6724.1224 | 6720.97 | 0 | 6775.7044 | 6651.7552 | 6878.7529 | 0 | 6577.3672
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 |  | 0.82 | 0.84 | 0.81 |  | 0.8 | 0.82 | 0.8 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.3 |  | 35.9 | 36.6 | 35.6 |  | 35.4 | 35.9 | 34.9 |  | 35.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.7 |  | 36.7 | 37.4 | 36.3 |  | 35.8 | 36.4 | 35.4 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.6 | 0 | 3.2 | 2.2 | 2.2 | 0 | 2.3 | 1.5 | 1.5 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.6 |  | 28.5 | 29.8 | 28.7 |  | 28.6 | 29.6 | 28.3 |  | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.1 |  | 33.5 | 35.2 | 34.1 |  | 33.5 | 34.9 | 33.9 |  | 33.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 5 | 5.4 | 5.4 | 0 | 4.9 | 5.3 | 5.6 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1293.6 |  | 1302.6 | 1279 | 1289.9 |  | 1296.9 | 1295.6 | 1290.8 |  | 1296.4
| HEAT CAPACITY | kW | 8226.9 | 0 | 8215.7044 | 0 | 7520.7852 | 7975.2887 | 8043.2564 | 0 | 7338.1178 | 7929.1917 | 8346.9746 | 0 | 7934.0878
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 | 0.46 | 0.46 |  | 0.46 | 0.46 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.6 |  | 18.7 | 19.8 | 19.5 |  | 19.4 | 19.8 | 18.9 |  | 19.6
| LIQUID LEVEL | mm | mm |  | 193.4 |  | 123.2 | 200.1 | 206.6 |  | 202.5 | 162.6 | 158.5 |  | 198
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.73 |  | 5.55 | 5.56 | 5.71 |  | 5.93 | 5.81 | 5.62 |  | 5.43
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 26
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-26
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 67.9 |  | 78.8 |  | 75.5 |  | 75.3 | 71.1 | 74 | 72.1 | 71.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.8 |  | 0 |  | 0 |  | 0.1 | 0 | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 61.9 |  | 73.6 |  | 71.2 |  | 69.9 | 67.9 | 68.6 | 66.3 | 66.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 68.7 |  | 70.6 |  | 63.5 |  | 65.6 | 75.1 | 75.3 | 73.3 | 73.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 35.8 |  | 52.8 |  | 40.2 |  | 35.1 | 67.9 | 53.7 | 39 | 44.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 116.4 |  | 118.5 |  | 118.8 |  | 117.3 | 117.1 | 118.8 | 116.8 | 117.4
| INPUT | Kw | 1194kW |  | 1142 |  | 1190 |  | 1209 |  | 1186 | 1184 | 1196 | 1182 | 1186
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50084 |  | 51235.3 |  | 49027.9 |  | 51398.2 | 50595.5 | 50585.2 | 50614.4 | 50604.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 59.9 |  | 59.2 |  | 57.9 |  | 57.5 | 58.9 | 58.7 | 59.2 | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 |  | 0.59 |  | 0.52 | 0.48 | 0.48 | 0.5 | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.9 |  | 45.1 |  | 45 |  | 44.8 | 44.9 | 44.9 | 44.9 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 |  | 0.22 |  | 0.22 | 0.23 | 0.23 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.7 |  | 3.5 |  | 4.1 |  | 3.8 | 4.6 | 4.6 | 4.8 | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 |  | 2.6 |  | 3.2 |  | 2.4 | 3.6 | 3.5 | 3.7 | 3.8
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | 2.3 | 0 | 0.7 | 0 | 1.6 | 1.3 | 1.3 | 1.2 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 666.2 |  | 647.6 |  | 641 |  | 622.6 | 641 | 654.1 | 641.8 | 638.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.7 |  | 13.8 |  | 13 |  | 13.2 | 13.9 | 13.7 | 13.3 | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 |  | 4.9 |  | 3.9 |  | 4 | 4.9 | 4.8 | 4.9 | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.7 | 0 | 8.9 | 0 | 9.1 | 0 | 9.2 | 9 | 8.9 | 8.4 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6692.7714 | 0 | 6655.4734 | 0 | 6735.6813 | 0 | 6614.2263 | 6661.6628 | 6722.2748 | 6225.3118 | 6268.0139
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.84 |  | 0.83 |  | 0.81 | 0.82 | 0.8 | 0.84 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 |  | 36.4 |  | 36.3 |  | 36.2 | 36.1 | 35.6 | 36.7 | 36.1
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 37.3 |  | 37 |  | 36.6 | 36.5 | 36 | 37.3 | 36.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.5 | 1 | 3.2 | 0 | 2.1 | 0 | 2.1 | 1.4 | 1.5 | 2.4 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.3 |  | 29.4 |  | 29.4 |  | 29.2 | 29.6 | 29.1 | 29.6 | 29.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.9 |  | 34.1 |  | 34.9 |  | 34.5 | 35.1 | 34.5 | 34.9 | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.6 | 0 | 4.7 | 0 | 5.5 | 0 | 5.3 | 5.5 | 5.4 | 5.3 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1300.7 |  | 1301.7 |  | 1293.5 |  | 1297.5 | 1279.8 | 1293.4 | 1297.4 | 1298.9
| HEAT CAPACITY | kW | 8226.9 | 0 | 8410.9931 | 0 | 7064.6536 | 0 | 8215.0693 | 0 | 7940.8199 | 8128.06 | 8065.0808 | 7940.2079 | 7949.388
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 |  | 0.46 |  | 0.46 | 0.46 | 0.46 | 0.48 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 |  | 19.5 |  | 19.4 |  | 19.5 | 19.8 | 19.3 | 20.4 | 20.2
| LIQUID LEVEL | mm | mm |  | 200.8 |  | 125.7 |  | 206 |  | 207.3 | 160.9 | 159.4 | 206 | 193.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.64 |  | 5.38 |  | 5.55 |  | 5.68 | 5.65 | 5.54 | 5.23 | 5.27
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 27
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-27
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 68.9 |  | 75.1 |  | 73.2 |  | 73.8 |  | 74 |  | 71.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 |  | 0 |  | 0.2 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.1 |  | 70.3 |  | 67.1 |  | 71.4 |  | 69.1 |  | 66.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.4 |  | 70.1 |  | 64.4 |  | 64.9 |  | 75.1 |  | 70
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.3 |  | 51.8 |  | 39.4 |  | 34.9 |  | 58.5 |  | 43.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.1 |  | 116.1 |  | 116.1 |  | 115.7 |  | 117 |  | 116.9
| INPUT | Kw | 1194kW |  | 1149 |  | 1167 |  | 1168 |  | 1180 |  | 1197 |  | 1188
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50093.4 |  | 51244.5 |  | 49036.8 |  | 51407.3 |  | 50605.9 |  | 50625
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.6 |  | 59.2 |  | 60.7 |  | 57.5 |  | 58.6 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 |  | 0.59 |  | 0.46 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 45.2 |  | 47.2 |  | 45.1 |  | 44.6 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.29 |  | 0.29 |  | 0.27 |  | 0.27 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 |  | 3.7 |  | 4.2 |  | 3.5 |  | 4.5 |  | 5
| SATURATION TEMPERATURE | CELCIUS | C |  | 8.5 |  | 8.6 |  | 6.8 |  | 7 |  | 3.4 |  | 3.9
| APPROACH TEMP | CELCIUS | C | 0 | -3.8 | 0 | -3.9 | 0 | -2.2 | 0 | -3.2 | 0 | 0.9 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 646.96 |  | 645.84 |  | 643.36 |  | 634.48 |  | 635.76 |  | 635.76
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.5 |  | 13.5 |  | 13.2 |  | 13.3 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 |  | 4.7 |  | 4.6 |  | 3.8 |  | 4.3 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.8 | 0 | 8.8 | 0 | 8.9 | 0 | 9.4 | 0 | 9 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6574.1894 | 0 | 6562.8083 | 0 | 6611.8984 | 0 | 6886.9654 | 0 | 6607.2055 | 0 | 6386.9654
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.3 |  | 0.3 |  | 0.28 |  | 0.28 |  | 0.81 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 |  | 36.3 |  | 36.3 |  | 36.1 |  | 35.7 |  | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 8.8 |  | 8.9 |  | 7.6 |  | 7.5 |  | 36.2 |  | 37.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | -24.8 | 1 | -24.4 | 0 | -26.1 | 0 | -25.8 | 0 | 2.9 | 0 | 3.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.5 |  | 28.3 |  | 28.4 |  | 28.2 |  | 28.3 |  | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.6 |  | 33.3 |  | 33.7 |  | 33.3 |  | 33.3 |  | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 0 | 5 | 0 | 5.3 | 0 | 5.1 | 0 | 5 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1302.98 |  | 1300.74 |  | 1297.1 |  | 1295.14 |  | 1291.08 |  | 1299.9
| HEAT CAPACITY | kW | 8226.9 | 0 | 7673.4388 | 0 | 7510.0462 | 0 | 7938.3718 | 0 | 7627.2679 | 0 | 7454.2725 | 0 | 8105.612
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 |  | 0.47 |  | 0.46 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 |  | 19.8 |  | 20 |  | 19.4 |  | 19.5 |  | 20.4
| LIQUID LEVEL | mm | mm |  | 202.7 |  | 133.3 |  | 206.3 |  | 208.9 |  | 154.4 |  | 196.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.69 |  | 5.61 |  | 5.7 |  | 5.62 |  | 5.79 |  | 5.43
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 28
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-28
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 68.9 |  | 77.3 | 75.5 | 74 |  | 75.8 | 78.1 | 76.1 |  | 72.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.1 |  | 72.1 | 70.1 | 68.8 |  | 70.6 | 71.1 | 70.9 |  | 66.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.4 |  | 68.8 | 65.3 | 63.1 |  | 65.6 | 76.4 | 73.8 |  | 71.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.3 |  | 54.7 | 42.4 | 40 |  | 35.9 | 57.2 | 58.5 |  | 39.3
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.1 |  | 114.7 | 116.2 | 116 |  | 115.2 | 115.9 | 117.2 |  | 114.8
| INPUT | Kw | 1194kW |  | 1149 |  | 1166 | 1185 | 1183 |  | 1180 | 1188 | 1196 |  | 1170
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50118.3 |  | 51254.9 | 49056.5 | 49047.5 |  | 51427.7 | 50625.4 | 50616.4 |  | 50635.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.6 |  | 59.1 | 57 | 57.6 |  | 44.5 | 58.6 | 45.1 |  | 59
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.52 | 0.45 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 44.9 | 44 | 45 |  | 45.1 | 44.9 | 45.1 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.29 |  | 0.21 | 0.22 | 0.27 |  | 0.23 | 0.22 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 |  | 3.2 | 4 | 4 |  | 3.5 | 4.1 | 4 |  | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 2.6 |  | 2.4 | 3.2 | 3.2 |  | 2.6 | 2.4 | 2.4 |  | 3.3
| APPROACH TEMP | CELCIUS | C | 0 | 2.1 | 0 | 1.9 | 0.9 | 1 | 0 | 1.3 | 1.9 | 1.6 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 646.96 |  | 645.68 | 643.1 | 639.76 |  | 637.92 | 619.8 | 634.24 |  | 641.92
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.2 | 13.2 | 12.7 |  | 13 | 13.7 | 13 |  | 12.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 |  | 4.3 | 4.1 | 4.2 |  | 3.9 | 4.3 | 4 |  | 4.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.8 | 0 | 8.9 | 9.1 | 8.5 | 0 | 9.1 | 9.4 | 9 | 0 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6574.1894 | 0 | 6635.7413 | 6757.7483 | 6279.3995 | 0 | 6703.3164 | 6727.6212 | 6591.4088 | 0 | 6226.4758
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.3 |  | 0.81 | 0.81 | 0.83 |  | 0.82 | 0.79 | 0.8 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 |  | 36.3 | 35.2 | 36 |  | 36.1 | 34.8 | 35.3 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.6 |  | 36.2 | 36.2 | 37 |  | 36.3 | 35.4 | 35.8 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2 | 1 | 2.3 | 2.5 | 3.7 | 0 | 2.9 | 1.5 | 2.3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.5 |  | 28.7 | 28.5 | 28.5 |  | 28.4 | 28.3 | 28.5 |  | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.6 |  | 33.9 | 33.7 | 33.3 |  | 33.4 | 33.9 | 33.5 |  | 33.8
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 0 | 5.2 | 5.2 | 4.8 | 0 | 5 | 5.6 | 5 | 0 | 5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1302.98 |  | 1297.24 | 1269.1 | 1298.36 |  | 1297.38 | 1246 | 1293.18 |  | 1293.32
| HEAT CAPACITY | kW | 8226.9 | 0 | 7673.4388 | 0 | 7789.4319 | 7620.4619 | 7196.4527 | 0 | 7490.6467 | 8057.2748 | 7466.3972 | 0 | 7467.2055
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.45 | 0.45 | 0.46 |  | 0.46 | 0.45 | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 |  | 19.1 | 19.1 | 19.4 |  | 19.4 | 18.8 | 18.9 |  | 19.8
| LIQUID LEVEL | mm | mm |  | 202.7 |  | 122.5 | 201.2 | 200.5 |  | 205.9 | 153.6 | 154.2 |  | 200.4
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.69 |  | 5.4 | 5.75 | 5.56 |  | 5.87 | 5.84 | 5.63 |  | 5.22
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 29
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-29
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.4 | 69.1 |  | 82.1 |  | 73.3 | 73.7 | 71.7 |  | 74.1 |  | 74
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.6 |  | 0 |  | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.5 | 63.4 |  | 77.8 |  | 68.7 | 68.8 | 66.6 |  | 69 |  | 68.4
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 66.1 | 68.7 |  | 70.3 |  | 64.9 | 65.9 | 66.1 |  | 75 |  | 73.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 42.6 | 38.5 |  | 77.8 |  | 41 | 36.2 | 32.2 |  | 56.3 |  | 42.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 116.5 | 114.6 |  | 117.4 |  | 116.1 | 113.3 | 112.7 |  | 116.1 |  | 116.8
| INPUT | Kw | 1194kW | 1150 | 1136 |  | 1191 |  | 1180 | 1161 | 1145 |  | 1183 |  | 1184
COMPRESSOR | RUNNING TIME | Hr | NA | 50136.5 | 50127.3 |  | 51264.4 |  | 49069.7 | 51446.5 | 51437.3 |  | 50636 |  | 50644.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.2 |  | 59.2 |  | 57.8 | 57.2 | 57.3 |  | 58.7 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.48 |  | 0.59 | 0.52 | 0.52 |  | 0.47 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 46 | 45 |  | 44.8 |  | 44.8 | 45.6 | 45 |  | 4.5 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.26 |  | 0.41 |  | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.8 | 4.4 |  | 3.1 |  | 4.2 | 3.6 | 3.6 |  | 4.5 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 3.3 | 3.6 |  | 2.1 |  | 3.3 | 2.9 | 2.7 |  | 3.5 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0.9 | 0.6 | 0 | 2.3 | 0 | 1.2 | 1.2 | 1.2 | 0 | 0.4 | 0 | 0.5
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 695.28 | 638.4 |  | 613.9 |  | 625.1 | 710.88 | 628.7 |  | 618.8 |  | 605.3
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.5 | 13.1 |  | 13.2 |  | 13.2 | 12.8 | 13.3 |  | 12.9 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.2 | 4.2 |  | 4.4 |  | 4.5 | 4.1 | 3.9 |  | 3.9 |  | 4.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.3 | 8.9 | 0 | 8.8 | 0 | 8.7 | 8.7 | 9.4 | 0 | 9 | 0 | 9.3
| CHILLING CAPACITY | kW | 7032.6kW | 6663.7691 | 6560.9238 | 0 | 6238.2448 | 0 | 6279.873 | 7141.6351 | 6824.2263 | 0 | 6430.9469 | 0 | 6500.3349
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.8 |  | 0.82 |  | 0.81 | 0.82 | 0.8 |  | 0.73 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.7 | 35.3 |  | 35.8 |  | 35.6 | 35 | 35.3 |  | 35 |  | 35.5
| SATURATED TEMEPRATURE | CELCIUS | C | 35.7 | 35.7 |  | 36.6 |  | 36.3 | 36.3 | 35.8 |  | 35.3 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.4 | 1.6 | 1 | 3.1 | 0 | 2.2 | 3 | 2.2 | 0 | 1.5 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.1 | 26.6 |  | 28.4 |  | 28.7 | 27.9 | 28.5 |  | 28.3 |  | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.3 | 34.1 |  | 33.5 |  | 34.1 | 33.3 | 33.6 |  | 33.8 |  | 33.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.2 | 7.5 | 0 | 5.1 | 0 | 5.4 | 5.4 | 5.1 | 0 | 5.5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1297.24 | 1293.3 |  | 1303.2 |  | 1293 | 1298.64 | 1293.4 | 1246 | 1269.6 |  | 1292
| HEAT CAPACITY | kW | 8226.9 | 7789.4319 | 11200.6351 | 0 | 7674.7344 | 0 | 8062.5866 | 8097.7552 | 7617.0208 | 0 | 8063.2794 | 0 | 7757.9677
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.46 |  | 0.45 |  | 0.45 | 0.46 | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.3 | 19.5 |  | 18.85 |  | 19.2 | 19.9 | 19.4 |  | 18.9 |  | 19.6
| LIQUID LEVEL | mm | mm | 188.4 | 198.5 |  | 127.5 |  | 204.1 | 202.2 | 205.1 |  | 157 |  | 192.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.53 | 5.71 |  | 5.42 |  | 5.68 | 5.78 | 5.76 |  | 5.67 |  | 5.57
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 30
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-04-30
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.6 |  | 81.7 | 76.3 | 74.7 |  | 74.5 | 77 | 77.7 |  | 77.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 |  | 0.1 | 0.2 | 0.3 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.2 |  | 78.1 | 71.7 | 69.6 |  | 69.9 | 71.9 | 73.4 |  | 73.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 68.8 |  | 69.3 | 63.8 | 63.8 |  | 66.6 | 73 | 75.1 |  | 72.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 39 |  | 54.8 | 39.4 | 41.4 |  | 36.6 | 56.4 | 56.3 |  | 42.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116 |  | 117 | 116.8 | 116 |  | 114.9 | 117.3 | 118.8 |  | 120.1
| INPUT | Kw | 1194kW |  | 1125 |  | 1187 | 1207 | 1185 |  | 1164 | 1201 | 1208 |  | 1217
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50145.3 |  | 51273.7 | 49087.4 | 49078.4 |  | 51458.9 | 50654.2 | 50645.3 |  | 50654.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59.4 | 57.8 | 58.7 |  | 57.2 | 44.8 | 58.6 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.48 | 0.59 | 0.58 |  | 0.52 | 0.48 | 0.47 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.7 |  | 44.9 | 44.9 | 44.6 |  | 44.7 | 44.9 | 44.9 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.26 |  | 0.41 | 0.23 | 0.22 |  | 0.21 | 0.23 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.2 |  | 3.1 | 4.4 | 4.2 |  | 3.5 | 4.4 | 4.4 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 18.5 | 3.4 | 3.1 |  | 3.1 | 0.23 | 3.5 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | -13.8 | 1.1 | 0.8 | 0 | 0.8 | 4.37 | 1 | 0 | 0.5
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 658.1 |  | 646.7 | 634.16 | 645.78 |  | 620.4 | 686.16 | 645.4 |  | 641.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.9 |  | 13.8 | 13.5 | 13 |  | 13.1 | 13.2 | 14 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 |  | 4.7 | 4.5 | 3.9 |  | 3.9 | 4.6 | 4.5 |  | 4.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.1 | 0 | 9.1 | 9 | 9.1 | 0 | 9.2 | 8.6 | 9.5 | 0 | 9.3
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6915.3695 | 0 | 6795.5774 | 6590.5774 | 6785.9099 | 0 | 6590.8545 | 6814.06 | 7080.0231 | 0 | 6890.1617
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.7 |  | 0.81 | 0.83 | 0.8 |  | 0.8 | 0.81 | 0.76 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 34.8 |  | 35.5 | 35.5 | 35.2 |  | 35 | 34.5 | 35 |  | 35.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.4 |  | 36.8 | 36.9 | 35.9 |  | 35.6 | 35.9 | 35.3 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.8 | 1 | 3.8 | 2.8 | 2.2 | 0 | 2.3 | 2.3 | 1.5 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.2 |  | 28.1 | 28.7 | 28.3 |  | 28.1 | 28.4 | 28.3 |  | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.6 |  | 33 | 34.1 | 33.7 |  | 33.3 | 33.6 | 33.8 |  | 33.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.4 | 0 | 4.9 | 5.4 | 5.4 | 0 | 5.2 | 5.2 | 5.5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1295.6 |  | 1304 | 1298.92 | 1296.7 |  | 1293.9 | 1294.02 | 1287.1 |  | 1291.9
| HEAT CAPACITY | kW | 8226.9 | 0 | 8078.7991 | 0 | 7378.291 | 8099.5012 | 8085.6582 | 0 | 7769.3764 | 7770.097 | 8174.4226 | 0 | 7757.3672
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.44 | 0.45 | 0.45 |  | 0.45 | 0.45 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.3 |  | 18.5 | 19.2 | 19 |  | 19 | 18.7 | 18.9 |  | 19.6
| LIQUID LEVEL | mm | mm |  | 193.8 |  | 120.1 | 203.1 | 203.8 |  | 207.1 | 153.2 | 157 |  | 192.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 6.03 |  | 5.62 | 5.64 | 5.67 |  | 5.82 | 5.41 | 5.67 |  | 5.57
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO