## 1
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-01
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 68.9 | 71.2 |  | 77.8 |  | 73.8 |  | 72.1 | 76.4 | 77.5 |  | 76.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 65.3 | 65.3 |  | 73.3 |  | 69.5 |  | 66 | 71.9 | 73.4 |  | 71.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 68.8 | 69.2 |  | 71.3 |  | 64.2 |  | 66.4 | 75.2 | 75.4 |  | 74
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 39 | 41.3 |  | 55.8 |  | 40.9 |  | 32.8 | 56.3 | 2.7 |  | 3.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 116.9 | 117.6 |  | 116.6 |  | 117.5 |  | 113 | 118.6 | 119.8 |  | 116
| INPUT | Kw | 1194kW | 1148 | 1148 |  | 1173 |  | 1186 |  | 1142 | 1208 | 1213 |  | 1141
COMPRESSOR | RUNNING TIME | Hr | NA | 50625.6 | 50616.2 |  | 51595.4 |  | 49547.8 |  | 51975.9 | 51156.3 | 51146.9 |  | 50965.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.4 | 58.8 |  | 59.3 |  | 57.7 |  | 57.2 | 58.7 | 58.7 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  | 0.58 |  | 0.52 | 0.45 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 44.8 |  | 44.9 |  | 44.9 |  | 45.1 | 44.9 | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.28 | 0.23 |  | 0.22 |  | 0.22 |  | 0.22 | 0.23 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.4 | 4.4 |  | 3.4 |  | 4.3 |  | 3.6 | 4.5 | 4.5 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 3.9 | 3.9 |  | 2.5 |  | 3.4 |  | 2.7 | 3.2 | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0.9 | 1 | 0 | 2.5 | 0 | 0.7 | 0 | 1.3 | 1.3 | 1.4 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 694.4 | 669.5 |  | 649.8 |  | 635.89 |  | 632.5 | 684.96 | 655.6 |  | 638.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.2 | 13.8 |  | 13.8 |  | 13.2 |  | 13.1 | 13.2 | 14.1 |  | 13.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.8 | 4.9 |  | 5 |  | 4.1 |  | 4 | 4.5 | 4.7 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.4 | 8.9 | 0 | 8.8 | 0 | 9.1 | 0 | 9.1 | 8.7 | 9.4 | 0 | 9.1
| CHILLING CAPACITY | kW | 7032.6kW | 6735.5196 | 6880.5427 | 0 | 6603.0485 | 0 | 6681.985 | 0 | 6646.3626 | 6881.2379 | 7116.2125 | 0 | 6708.3603
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.8 |  | 0.82 |  | 0.81 |  | 0.8 | 0.8 | 0.8 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.6 | 35.3 |  | 35.7 |  | 35.4 |  | 35.1 | 34.2 | 34.8 |  | 35.3
| SATURATED TEMEPRATURE | CELCIUS | C | 35.9 | 35.8 |  | 36.6 |  | 36.1 |  | 35.6 | 35.5 | 35.3 |  | 36.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.4 | 1.7 | 1 | 3.2 | 0 | 2.2 | 0 | 2.3 | 2.3 | 1.6 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.3 | 28.5 |  | 28.5 |  | 28.5 |  | 28.4 | 28 | 28.1 |  | 28.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.5 | 34.1 |  | 33.4 |  | 33.9 |  | 33.3 | 33.2 | 33.7 |  | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.2 | 5.6 | 0 | 4.9 | 0 | 5.4 | 0 | 4.9 | 5.2 | 5.6 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1297.66 | 1296.9 |  | 1300.2 |  | 1298.8 |  | 1297.2 | 1290.24 | 1289 |  | 1300.2
| HEAT CAPACITY | kW | 8226.9 | 7791.9538 | 8386.4203 | 0 | 7356.7898 | 0 | 8098.7529 | 0 | 7339.8152 | 7747.3995 | 8335.3349 | 0 | 7957.3441
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.46 |  | 0.45 |  | 0.45 |  | 0.46 | 0.45 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19 | 19.6 |  | 19 |  | 19.1 |  | 19.3 | 19 | 18.9 |  | 19.6
| LIQUID LEVEL | mm | mm | 153.9 | 197.7 |  | 130.4 |  | 216.9 |  | 218.9 | 153.9 | 163.8 |  | 200.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.45 | 5.73 |  | 5.51 |  | 5.65 |  | 5.9 | 5.45 | 5.78 |  | 5.53
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 2
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-02
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 69.7 |  | 81.7 | 74.1 | 73.9 | 73.2 | 76 |  | 78 |  | 73.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 |  | 0 | 0 | 0 | 0.1 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.3 |  | 78.3 | 70.1 | 69.1 | 70 | 71.5 |  | 74 |  | 68.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.4 |  | 69.9 | 64.6 | 64.6 | 67.5 | 68.6 |  | 73.8 |  | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 38.8 |  | 57.3 | 37.4 | 41.6 | 35.2 | 36.2 |  | 56.1 |  | 45.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.4 |  | 117.9 | 118.2 | 115.8 | 116.4 | 117.2 |  | 119.1 |  | 116.3
| INPUT | Kw | 1194kW |  | 1123 |  | 1194 | 1208 | 1167 | 1186 | 1190 |  | 1205 |  | 1175
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50637.9 |  | 51605.7 | 4566.8 | 49557.9 | 51994.7 | 51985.8 |  | 51167 |  | 50975.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59.2 | 57.8 | 57.7 | 57.4 | 57.3 |  | 58.5 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.48 | 0.59 | 0.58 | 0.52 | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 45 | 45.3 | 45 | 45 | 44.9 |  | 45 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.22 | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.1 |  | 3 | 4.2 | 3.9 | 3.8 | 3.9 |  | 3.9 |  | 4.4
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.7 |  | 2.1 | 3.4 | 3.1 | 2.8 | 2.8 |  | 2.9 |  | 3.3
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 0 | 2.5 | 1.2 | 0.8 | 1.5 | 1.4 | 0 | 1.3 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 653.4 |  | 635.9 | 638.4 | 638.1 | 619.9 | 626.4 |  | 635.6 |  | 636.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.8 |  | 13.6 | 13.6 | 13.1 | 13.9 | 13.7 |  | 13.7 |  | 13.1
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.6 | 4.6 | 3.9 | 4.3 | 4.2 |  | 4.2 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.2 | 0 | 9 | 9 | 9.2 | 9.6 | 9.5 | 0 | 9.5 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6941.4319 | 0 | 6608.6605 | 6634.642 | 6778.8915 | 6871.8707 | 6871.5935 | 0 | 6972.5173 | 0 | 6321.8938
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 |  | 0.82 | 0.84 | 0.8 | 0.88 | 0.8 |  | 0.8 |  | 0.8
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 34.9 |  | 35.5 | 36.5 | 35.3 | 36.4 | 35.3 |  | 34.5 |  | 35
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.4 |  | 36.4 | 37.3 | 36 | 36.9 | 35.8 |  | 35.1 |  | 35.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.6 | 0 | 3.2 | 2.2 | 2.2 | 2.2 | 2.3 | 0 | 1.6 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.3 |  | 28.2 | 29.6 | 28.4 | 39.5 | 28.2 |  | 28.1 |  | 28
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.8 |  | 33.2 | 35.1 | 33.8 | 34.7 | 33.5 |  | 33.5 |  | 33.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 5 | 5.5 | 5.4 | -4.8 | 5.3 | 0 | 5.4 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1300.3 |  | 1301.9 | 1298.3 | 1300.9 | 1294.8 | 1297.1 |  | 1288.4 |  | 1299.8
| HEAT CAPACITY | kW | 8226.9 | 0 | 8258.2564 | 0 | 7516.7436 | 8245.5543 | 8111.8476 | -7176.7206 | 7938.3718 | 0 | 8033.903 | 0 | 8104.9885
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.44 | 0.46 | 0.45 | 0.46 | 0.45 |  | 0.44 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.4 |  | 18.8 | 19.7 | 19.1 | 19.3 | 19.2 |  | 18.5 |  | 19.4
| LIQUID LEVEL | mm | mm |  | 202.8 |  | 117 | 194.3 | 202.7 | 205.5 | 223.6 |  | 167.9 |  | 197.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 6 |  | 5.6 | 5.54 | 5.84 | 5.57 | 5.89 |  | 5.8 |  | 5.49
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 3
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-03
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 77.4 | 72.1 |  | 81.4 |  | 73.8 |  | 75.3 | 81.9 | 75.6 |  | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.1 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 73 | 65.9 |  | 77.9 |  | 70.1 |  | 72 | 77.9 | 70.4 |  | 70.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 65.2 | 69 |  | 69.7 |  | 64.9 |  | 68.2 | 72 | 75 |  | 73.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 42.7 | 38.5 |  | 57.1 |  | 41.3 |  | 35.6 | 58 | 58 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 119.4 | 117.1 |  | 118.4 |  | 115.7 |  | 117.6 | 119.8 | 117.7 |  | 118.6
| INPUT | Kw | 1194kW | 1169 | 1150 |  | 1197 |  | 1175 |  | 1194 | 1216 | 1194 |  | 1200
COMPRESSOR | RUNNING TIME | Hr | NA | 50656.9 | 50647.5 |  | 51615 |  | 49577.5 |  | 52009.5 | 51185.7 | 51176 |  | 50984.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.2 |  | 59.3 |  | 57.7 |  | 57.5 | 58.4 | 58.7 |  | 59
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  | 0.58 |  | 0.52 | 0.47 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 45.1 |  | 44.8 |  | 45.1 |  | 44.8 | 44.9 | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.23 |  | 0.21 |  | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.6 | 4.2 |  | 3.2 |  | 4 |  | 4 | 3.8 | 4.3 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C | 3.3 | 3.7 |  | 2.3 |  | 3.3 |  | 2.8 | 3.3 | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0.9 | 1 | 0 | 2.4 | 0 | 0.7 | 0 | 1.6 | 0.8 | 1.3 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 697.8 | 642.2 |  | 631.9 |  | 635.44 |  | 627.8 | 687.9 | 642.9 |  | 639.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.1 | 13.8 |  | 13.8 |  | 13.2 |  | 13.7 | 13 | 13.9 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.2 | 4.7 |  | 4.7 |  | 4 |  | 4.4 | 4.1 | 4.6 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.9 | 9.1 | 0 | 9.1 | 0 | 9.2 | 0 | 9.3 | 8.9 | 9.3 | 0 | 9
| CHILLING CAPACITY | kW | 7032.6kW | 7171.3857 | 6748.291 | 0 | 6640.0577 | 0 | 6750.6328 | 0 | 6741.963 | 7069.642 | 6904.1224 | 0 | 6645.0346
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.79 | 0.8 |  | 0.82 |  | 0.81 |  | 0.81 | 0.79 | 0.79 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.6 | 35.3 |  | 35.9 |  | 35.6 |  | 35.6 | 34 | 34.8 |  | 35.5
| SATURATED TEMEPRATURE | CELCIUS | C | 35.2 | 35.8 |  | 36.8 |  | 36.3 |  | 36.1 | 34.7 | 35.3 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.8 | 1.7 | 0 | 3.3 | 0 | 2.2 | 0 | 2.2 | 1.5 | 1.5 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.9 | 28.6 |  | 28.5 |  | 28.7 |  | 28.7 | 27.6 | 28.3 |  | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.4 | 34.1 |  | 33.5 |  | 34.1 |  | 33.9 | 33.2 | 33.8 |  | 33.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.5 | 0 | 5 | 0 | 5.4 | 0 | 5.2 | 5.6 | 5.5 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1288.8 | 1296.1 |  | 1290.6 |  | 1304.9 |  | 1293.9 | 1299.1 | 1291.9 |  | 1294.6
| HEAT CAPACITY | kW | 8226.9 | 8185.2194 | 8231.582 | 0 | 7451.5012 | 0 | 8136.7898 | 0 | 7769.3764 | 8400.6467 | 8204.9076 | 0 | 7923.0716
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.44 | 0.46 |  | 0.45 |  | 0.45 |  | 0.46 | 0.48 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 18.5 | 19.5 |  | 18.7 |  | 19.3 |  | 19.2 | 18 | 19.6 |  | 19.6
| LIQUID LEVEL | mm | mm | 203.2 | 202.9 |  | 122.5 |  | 205.4 |  | 214.9 | 162.3 | 160.3 |  | 199
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.58 | 5.84 |  | 5.61 |  | 5.79 |  | 5.74 | 5.38 | 5.74 |  | 5.52
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 4
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-04
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 67.8 |  | 75.2 | 74.3 | 74 | 78.5 | 74 |  | 73.4 |  | 72.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 | 0 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 60.7 |  | 69.6 | 70.7 | 69.5 | 74.8 | 69.1 |  | 68.7 |  | 66.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.4 |  | 70.9 | 63.6 | 63.7 | 67.2 | 67.6 |  | 73.5 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.4 |  | 49.1 | 35.7 | 36.1 | 33.7 | 34.6 |  | 50 |  | 43
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.3 |  | 113.8 | 117.5 | 118 | 118.6 | 116.9 |  | 117.5 |  | 117.3
| INPUT | Kw | 1194kW |  | 1148 |  | 1164 | 1208 | 1205 | 1221 | 1190 |  | 1199 |  | 1192
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50661.1 |  | 51620 | 49597.4 | 495779 | 52029.6 | 52012 |  | 51181 |  | 50992
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 |  | 59.3 | 57.9 | 57.7 | 57.4 | 57.5 |  | 58.7 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.7 |  | 44.9 | 45 | 45 | 45.1 | 44.9 |  | 44.9 |  | 45.2
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.21 |  | 0.22 | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.9 |  | 3.6 | 4.3 | 4.2 | 4 | 4 |  | 4.5 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.5 |  | 2.7 | 3.5 | 3.4 | 2.8 | 3 |  | 3.7 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0 | 2.2 | 0.7 | 0.6 | 1.3 | 1.4 | 0 | 0.9 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 677.7 |  | 629.3 | 630.6 | 641.2 | 627.5 | 619.8 |  | 634.9 |  | 638.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.9 |  | 13.5 | 13.3 | 13.1 | 13.6 | 13.6 |  | 13.9 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5.3 |  | 4.9 | 4.2 | 4 | 4.1 | 4.4 |  | 4.6 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.6 | 0 | 8.6 | 9.1 | 9.1 | 9.5 | 9.2 | 0 | 9.3 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6730.0462 | 0 | 6249.3995 | 6626.3972 | 6737.7829 | 6883.6605 | 6584.4804 | 0 | 6818.2102 | 0 | 6413.4873
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 | 0.85 | 0.84 | 0.84 | 0.84 |  | 0.82 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.5 |  | 36.8 | 36.9 | 36.8 | 37 | 36.7 |  | 36.1 |  | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.9 |  | 37.6 | 37.6 | 37.4 | 37.4 | 37.2 |  | 36.4 |  | 37.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.6 | 1 | 3.1 | 2.1 | 2.1 | 2.2 | 2.2 | 0 | 1.5 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.8 |  | 29.8 | 30 | 29.9 | 30 | 29.8 |  | 29.7 |  | 29.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 35.3 |  | 34.5 | 35.5 | 35.3 | 35.2 | 35 |  | 34.9 |  | 34.8
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 4.7 | 5.5 | 5.4 | 5.2 | 5.2 | 0 | 5.2 | 0 | 5.1
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1291.4 |  | 1301 | 1296.5 | 1296.7 | 1299.1 | 1295.2 |  | 1293.6 |  | 1297
| HEAT CAPACITY | kW | 8226.9 | 0 | 8201.7321 | 0 | 7060.8545 | 8234.1224 | 8085.6582 | 7800.6005 | 7777.1824 | 0 | 7767.5751 | 0 | 7638.2217
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 |  | 0.46 | 0.47 | 0.47 | 0.47 | 0.47 |  | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.7 |  | 19.9 | 19.9 | 19.9 | 19.9 | 20.1 |  | 19.2 |  | 20.3
| LIQUID LEVEL | mm | mm |  | 196.5 |  | 127.5 | 207.9 | 212.7 | 216.9 | 214.8 |  | 160 |  | 199
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.52 |  | 5.49 | 5.55 | 5.54 | 5.69 | 5.82 |  | 5.6 |  | 5.29
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 5
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-05
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.6 | 71 |  | 81.1 |  | 71.8 |  | 77.4 | 74.6 | 77.2 |  | 74.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.6 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.5 | 65.1 |  | 77.7 |  | 67.5 |  | 74.8 | 71.7 | 71.9 |  | 68.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.3 | 68 |  | 69.9 |  | 63.6 |  | 67.1 | 76 | 73.9 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 37.5 | 40 |  | 51.6 |  | 37.9 |  | 38.8 | 56.3 | 54.5 |  | 44.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118.1 | 117.2 |  | 117.9 |  | 116.2 |  | 120 | 117.5 | 118.8 |  | 118.3
| INPUT | Kw | 1194kW | 1162 | 1153 |  | 1198 |  | 1174 |  | 1218 | 1194 | 1207 |  | 1194
COMPRESSOR | RUNNING TIME | Hr | NA | 50684 | 50674.7 |  | 51633.9 |  | 49610.4 |  | 52042.5 | 51218.6 | 51209.3 |  | 51002.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.2 |  | 59.3 |  | 57.5 |  | 57.2 | 58.5 | 58.7 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  | 0.59 |  | 0.52 | 0.47 | 0.47 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 44.8 |  | 45.1 |  | 44.8 |  | 45.1 | 45.1 | 44.9 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.23 |  | 0.21 |  | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4 | 4.3 |  | 3.2 |  | 4.2 |  | 4.2 | 4.2 | 4.4 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 3.4 | 3.8 |  | 2.3 |  | 3.5 |  | 3.2 | 3.1 | 3.2 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0.9 | 1 | 0 | 2.3 | 0 | 0.7 | 0 | 1.3 | 1.2 | 1.3 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 650 | 668.1 |  | 645.2 |  | 619.6 |  | 664.1 | 635.1 | 650.2 |  | 638
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.6 | 13.5 |  | 13.6 |  | 13.4 |  | 13.7 | 13.8 | 13.7 |  | 13.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 4.8 |  | 4.6 |  | 4.2 |  | 4.5 | 4.3 | 4.5 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9.3 | 8.7 | 0 | 9 | 0 | 9.2 | 0 | 9.2 | 9.5 | 9.2 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 6980.3695 | 6711.8591 | 0 | 6705.3118 | 0 | 6582.3557 | 0 | 7055.1039 | 6967.0323 | 6907.4365 | 0 | 6483.1409
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.81 |  | 0.83 |  | 0.82 |  | 0.82 | 0.85 | 0.86 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.6 | 35.7 |  | 36.2 |  | 35.9 |  | 36.1 | 35.1 | 35.4 |  | 35.9
| SATURATED TEMEPRATURE | CELCIUS | C | 36.1 | 36.1 |  | 37 |  | 36.6 |  | 36.6 | 35.6 | 35.8 |  | 36.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 1.6 | 1 | 3.2 | 0 | 2.1 | 0 | 2.3 | 1.6 | 1.5 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29 | 29 |  | 29 |  | 29.1 |  | 29 | 28.7 | 28.8 |  | 28.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.4 | 34.5 |  | 33.8 |  | 34.5 |  | 34.3 | 34 | 34.3 |  | 34.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.4 | 5.5 | 0 | 4.8 | 0 | 5.4 | 0 | 5.3 | 5.3 | 5.5 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1300.2 | 1303.2 |  | 1299.2 |  | 1304.3 |  | 1300 | 1290.4 | 1288.3 |  | 1299.4
| HEAT CAPACITY | kW | 8226.9 | 8107.4827 | 8276.6744 | 0 | 7201.1085 | 0 | 8133.0485 | 0 | 7956.1201 | 7897.3672 | 8182.0439 | 0 | 7952.448
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.46 |  | 0.45 |  | 0.46 |  | 0.46 | 0.45 | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.4 | 19.7 |  | 19.1 |  | 19.5 |  | 19.6 | 18.9 | 19.1 |  | 20.1
| LIQUID LEVEL | mm | mm | 194.2 | 197.5 |  | 123.2 |  | 204.5 |  | 193.2 | 158 | 159.1 |  | 197.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.86 | 5.65 |  | 5.55 |  | 5.76 |  | 5.64 | 5.81 | 5.58 |  | 5.49
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 6
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-06
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.6 |  | 77.4 | 73.8 | 74.3 |  | 75.7 | 81.9 | 74.3 |  | 73.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.9 |  | 72.1 | 70.1 | 68.4 |  | 72.4 | 77.9 | 69.2 |  | 68.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.8 |  | 70.7 | 64.9 | 64.7 |  | 67.6 | 72 | 74.6 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.9 |  | 49.4 | 41.3 | 36.1 |  | 33.4 | 58 | 53.6 |  | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.1 |  | 116.2 | 115.7 | 117.4 |  | 118.9 | 119.8 | 118.9 |  | 119.3
| INPUT | Kw | 1194kW |  | 1147 |  | 1175 | 1175 | 1176 |  | 1204 | 1216 | 1200 |  | 1202
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50694.7 |  | 51643.8 | 49628.2 | 49620.1 |  | 52052.5 | 51239.3 | 51231.9 |  | 51012.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 |  | 59.2 | 57.7 | 57.6 |  | 57.5 | 58.4 | 58.7 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 | 0.58 | 0.59 |  | 0.52 | 0.47 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 45 | 45.1 | 44.9 |  | 45 | 44.9 | 44.9 |  | 44.7
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.23 | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.6 | 4 | 3.9 |  | 4.1 | 3.8 | 4.4 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 |  | 2.7 | 3.3 | 3.3 |  | 3 | 3.3 | 3.3 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 0.5 | 0 | 2.2 | 0.7 | 1.3 | 0 | 1 | 0.8 | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 628.88 |  | 631.92 | 635.44 | 638 |  | 634.64 | 687.9 | 637.68 |  | 646.72
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.5 | 13.2 | 13.4 |  | 13.5 | 13 | 13.4 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.4 |  | 4.9 | 4 | 4.6 |  | 4 | 4.1 | 4.4 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.1 | 0 | 8.6 | 9.2 | 8.8 | 0 | 9.5 | 8.9 | 9 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6608.3233 | 0 | 6275.418 | 6750.6328 | 6483.1409 | 0 | 6961.9861 | 7069.642 | 6627.1594 | 0 | 6422.3926
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 | 0.81 | 0.84 |  | 0.84 | 0.79 | 0.82 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.2 |  | 36.6 | 35.6 | 36.5 |  | 36.6 | 34 | 35.8 |  | 36.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.7 |  | 37.5 | 36.3 | 37.2 |  | 37.1 | 34.7 | 36.3 |  | 37.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.3 | 1 | 3.6 | 2.2 | 2.8 | 0 | 3 | 1.5 | 2.3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.2 |  | 29 | 28.7 | 29 |  | 28.9 | 27.6 | 29 |  | 29.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.4 |  | 33.9 | 34.1 | 34.4 |  | 34.1 | 33.2 | 34 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 0 | 4.9 | 5.4 | 5.4 | 0 | 5.2 | 5.6 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1301.16 |  | 1300.6 | 1304.9 | 1306.76 |  | 1288.98 | 1299.1 | 1291.22 |  | 1297.94
| HEAT CAPACITY | kW | 8226.9 | 0 | 7812.97 | 0 | 7359.0531 | 8136.7898 | 8148.388 | 0 | 7739.8337 | 8400.6467 | 7455.0808 | 0 | 7793.6351
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.45 | 0.47 |  | 0.46 | 0.48 | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 |  | 19.8 | 19.3 | 19.9 |  | 19.8 | 18 | 19.5 |  | 20.3
| LIQUID LEVEL | mm | mm |  | 189.3 |  | 127 | 205.4 | 209.5 |  | 216 | 162.3 | 160.5 |  | 201.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.77 |  | 5.59 | 5.79 | 5.65 |  | 5.72 | 5.38 | 5.63 |  | 5.22
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 7
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-07
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 74.1 | 72.1 |  | 81.4 |  | 73.8 |  | 75.3 | 77.5 | 75.6 |  | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.1 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 69.5 | 65.9 |  | 77.9 |  | 70.1 |  | 72 | 72.9 | 70.4 |  | 70.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 66.3 | 69 |  | 69.7 |  | 64.9 |  | 68.2 | 71.7 | 75 |  | 73.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 40.8 | 38.5 |  | 57.1 |  | 41.3 |  | 35.6 | 53.3 | 58 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 119.7 | 117.1 |  | 118.4 |  | 115.7 |  | 117.6 | 119.6 | 117.7 |  | 118.6
| INPUT | Kw | 1194kW | 1176 | 1150 |  | 1197 |  | 1175 |  | 1194 | 1211 | 1194 |  | 1200
COMPRESSOR | RUNNING TIME | Hr | NA | 50714.9 | 50703.9 |  | 51653.6 |  | 49642.7 |  | 52076.6 | 51252.8 | 51241.7 |  | 51022.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.8 | 58.2 |  | 59.3 |  | 57.7 |  | 57.5 | 58.6 | 58.7 |  | 59
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  | 0.58 |  | 0.52 | 0.48 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.7 | 45.1 |  | 44.8 |  | 45.1 |  | 44.8 | 45.6 | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.21 |  | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.2 | 4.2 |  | 3.2 |  | 4 |  | 4 | 4.3 | 4.3 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C | 3.6 | 3.7 |  | 2.3 |  | 3.3 |  | 2.8 | 3.2 | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 1 | 1 | 0 | 2.4 | 0 | 0.7 | 0 | 1.6 | 1.4 | 1.3 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 695.7 | 642.2 |  | 631.9 |  | 635.44 |  | 627.8 | 689 | 642.9 |  | 639.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.3 | 13.8 |  | 13.8 |  | 13.2 |  | 13.7 | 13.4 | 13.9 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.6 | 4.7 |  | 4.7 |  | 4 |  | 4.4 | 4.6 | 4.6 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.7 | 9.1 | 0 | 9.1 | 0 | 9.2 | 0 | 9.3 | 8.8 | 9.3 | 0 | 9
| CHILLING CAPACITY | kW | 7032.6kW | 6989.1339 | 6748.291 | 0 | 6640.0577 | 0 | 6750.6328 | 0 | 6741.963 | 7001.3857 | 6904.1224 | 0 | 6645.0346
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.8 |  | 0.82 |  | 0.81 |  | 0.81 | 0.81 | 0.79 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.9 | 35.3 |  | 35.9 |  | 35.6 |  | 35.6 | 35.4 | 34.8 |  | 35.5
| SATURATED TEMEPRATURE | CELCIUS | C | 36.8 | 35.8 |  | 36.8 |  | 36.3 |  | 36.1 | 35.9 | 35.3 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.1 | 1.7 | 0 | 3.3 | 0 | 2.2 | 0 | 2.2 | 1.6 | 1.5 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.1 | 28.6 |  | 28.5 |  | 28.7 |  | 28.7 | 28.9 | 28.3 |  | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.7 | 34.1 |  | 33.5 |  | 34.1 |  | 33.9 | 34.3 | 33.8 |  | 33.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 5.5 | 0 | 5 | 0 | 5.4 | 0 | 5.2 | 5.4 | 5.5 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1299.9 | 1296.1 |  | 1290.6 |  | 1304.9 |  | 1293.9 | 1300.9 | 1291.9 |  | 1294.6
| HEAT CAPACITY | kW | 8226.9 | 8405.8199 | 8231.582 | 0 | 7451.5012 | 0 | 8136.7898 | 0 | 7769.3764 | 8111.8476 | 8204.9076 | 0 | 7923.0716
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.46 |  | 0.45 |  | 0.45 |  | 0.46 | 0.45 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.6 | 19.5 |  | 18.7 |  | 19.3 |  | 19.2 | 19.2 | 19.6 |  | 19.6
| LIQUID LEVEL | mm | mm | 195.1 | 202.9 |  | 122.5 |  | 205.4 |  | 214.9 | 159.6 | 160.3 |  | 199
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.45 | 5.84 |  | 5.61 |  | 5.79 |  | 5.74 | 5.42 | 5.74 |  | 5.52
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 8
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-08
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 72.1 |  | 80.8 | 75.9 | 75.3 | 78.1 | 75.4 |  | 74.3 |  | 74
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.9 |  | 76.9 | 70.7 | 71 | 74.7 | 70.4 |  | 71 |  | 68.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 70.1 |  | 69.4 | 63.5 | 64.6 | 66.3 | 68.7 |  | 74.4 |  | 76.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.6 |  | 53.1 | 37.9 | 39.4 | 37.6 | 34.5 |  | 45 |  | 45.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.6 |  | 117.5 | 118.3 | 117.7 | 121.8 | 117.1 |  | 117.4 |  | 117.8
| INPUT | Kw | 1194kW |  | 1147 |  | 1194 | 1203 | 1191 | 1235 | 1192 |  | 1197 |  | 1191
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50719.7 |  | 51663.4 | 49665.9 | 49652.2 | 52100 | 52086.3 |  | 51265.8 |  | 51031.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 |  | 59.2 | 57.9 | 57.9 | 57.5 | 57.5 |  | 58.5 |  | 59
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 | 0.59 | 0.58 | 0.59 | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 |  | 45 | 45 | 44.9 | 44.9 | 44.8 |  | 45 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.23 | 0.23 | 0.23 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.1 |  | 3.3 | 4.2 | 4 | 4.5 | 4.1 |  | 4.5 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.3 |  | 2 | 3.3 | 3.3 | 3.5 | 2.8 |  | 2.8 |  | 3.2
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | 2.1 | 1.1 | 1.2 | 1.1 | 1.1 | 0 | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 644.48 |  | 633.04 | 636.88 | 629.52 | 709.12 | 623.68 |  | 636.4 |  | 635.76
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.2 |  | 13 | 13.4 | 13.5 | 13.5 | 13.6 |  | 13 |  | 12.9
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.3 |  | 4.1 | 4.4 | 4.5 | 4.6 | 3.9 |  | 3.9 |  | 4.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.9 | 0 | 8.9 | 9 | 9 | 8.9 | 9.7 | 0 | 9.1 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6623.4088 | 0 | 6505.8383 | 6618.8453 | 6542.3557 | 7287.7229 | 6985.7921 | 0 | 6687.3441 | 0 | 6386.9654
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.79 |  | 0.81 | 0.83 | 0.8 | 0.84 | 0.79 |  | 0.77 |  | 0.8
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.6 |  | 36.2 | 36.4 | 35.9 | 36.5 | 36 |  | 35.3 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.1 |  | 36 | 36.9 | 35.6 | 37 | 35.4 |  | 34.6 |  | 35.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.5 | 0 | 3.7 | 2.9 | 2.8 | 3 | 2.9 | 0 | 2.4 | 0 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.5 |  | 27.3 | 28.7 | 27.4 | 28.5 | 27.1 |  | 27.2 |  | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 32.6 |  | 32.3 | 34 | 32.8 | 34 | 32.5 |  | 32.2 |  | 32.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 0 | 5 | 5.3 | 5.4 | 5.5 | 5.4 | 0 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1287.86 |  | 1296.4 | 1293.32 | 1295 | 1295 | 1299.2 |  | 1291.36 |  | 1293.6
| HEAT CAPACITY | kW | 8226.9 | 0 | 7584.3949 | 0 | 7484.9885 | 7915.2379 | 8075.0577 | 8224.5958 | 8101.2471 | 0 | 7455.8891 | 0 | 7767.5751
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 | 0.46 | 0.46 | 0.47 | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.7 |  | 19.1 | 19.5 | 19.2 | 20.6 | 19.6 |  | 19.1 |  | 20
| LIQUID LEVEL | mm | mm |  | 197.5 |  | 132.2 | 208 | 207.1 | 208.2 | 219.1 |  | 162.5 |  | 195.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.93 |  | 5.57 | 5.64 | 5.64 | 5.09 | 5.7 |  | 5.8 |  | 5.57
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 9
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-09
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.3 | 72.1 |  | 80.8 |  | 75.3 |  | 75.4 | 78.5 | 74.3 |  | 74
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.1 |  | 0 |  | 0 |  | 0 | 0.2 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 67.8 | 66.9 |  | 76.9 |  | 71 |  | 70.4 | 74.6 | 71 |  | 68.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.6 | 70.1 |  | 69.4 |  | 64.6 |  | 68.7 | 74 | 74.4 |  | 76.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 39.4 | 37.6 |  | 53.1 |  | 39.4 |  | 34.5 | 46 | 45 |  | 45.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 117 | 117.6 |  | 117.5 |  | 117.7 |  | 117.1 | 118.5 | 117.4 |  | 117.8
| INPUT | Kw | 1194kW | 1145 | 1147 |  | 1194 |  | 1191 |  | 1192 | 1211 | 1197 |  | 1191
COMPRESSOR | RUNNING TIME | Hr | NA | 50738.2 | 50719.7 |  | 51663.4 |  | 49652.2 |  | 52086.3 | 51284.5 | 51265.8 |  | 51031.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.8 | 58.4 |  | 59.2 |  | 57.9 |  | 57.5 | 58.3 | 58.5 |  | 59
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  | 0.58 |  | 0.52 | 0.47 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 45 |  | 45 |  | 44.9 |  | 44.8 | 45 | 45 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.21 |  | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.1 | 4.1 |  | 3.3 |  | 4 |  | 4.1 | 4.3 | 4.5 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 3.6 | 3.3 |  | 2 |  | 3.3 |  | 2.8 | 3.2 | 2.8 |  | 3.2
| APPROACH TEMP | CELCIUS | C | 1 | 1 | 0 | 2.1 | 0 | 1.2 | 0 | 1.1 | 1.2 | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 671.92 | 644.48 |  | 633.04 |  | 629.52 |  | 623.68 | 662.16 | 636.4 |  | 635.76
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.4 | 13.2 |  | 13 |  | 13.5 |  | 13.6 | 13.5 | 13 |  | 12.9
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.6 | 4.3 |  | 4.1 |  | 4.5 |  | 3.9 | 4.4 | 3.9 |  | 4.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.8 | 8.9 | 0 | 8.9 | 0 | 9 | 0 | 9.7 | 9.1 | 9.1 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 6827.8245 | 6623.4088 | 0 | 6505.8383 | 0 | 6542.3557 | 0 | 6985.7921 | 6958.0323 | 6687.3441 | 0 | 6386.9654
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.79 |  | 0.81 |  | 0.8 |  | 0.79 | 0.79 | 0.77 |  | 0.8
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.9 | 35.6 |  | 36.2 |  | 35.9 |  | 36 | 34.5 | 35.3 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C | 35.6 | 35.1 |  | 36 |  | 35.6 |  | 35.4 | 35.2 | 34.6 |  | 35.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.4 | 2.5 | 0 | 3.7 | 0 | 2.8 | 0 | 2.9 | 2.3 | 2.4 | 0 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.9 | 27.5 |  | 27.3 |  | 27.4 |  | 27.1 | 27.7 | 27.2 |  | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.2 | 32.6 |  | 32.3 |  | 32.8 |  | 32.5 | 32.9 | 32.2 |  | 32.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.3 | 5.1 | 0 | 5 | 0 | 5.4 | 0 | 5.4 | 5.2 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1289.96 | 1287.86 |  | 1296.4 |  | 1295 |  | 1299.2 | 1302.42 | 1291.36 |  | 1293.6
| HEAT CAPACITY | kW | 8226.9 | 7894.6744 | 7584.3949 | 0 | 7484.9885 | 0 | 8075.0577 | 0 | 8101.2471 | 7820.5358 | 7455.8891 | 0 | 7767.5751
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.46 |  | 0.45 |  | 0.46 |  | 0.46 | 0.44 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.3 | 19.7 |  | 19.1 |  | 19.2 |  | 19.6 | 18.5 | 19.1 |  | 20
| LIQUID LEVEL | mm | mm | 199.5 | 197.5 |  | 132.2 |  | 207.1 |  | 219.1 | 157 | 162.5 |  | 195.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.86 | 5.93 |  | 5.57 |  | 5.64 |  | 5.7 | 5.72 | 5.8 |  | 5.57
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 10
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-10
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.6 |  | 77.4 | 75.5 | 74.3 | 75.2 | 75.7 |  | 74.3 |  | 73.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.9 |  | 72.1 | 70.1 | 68.4 | 72.7 | 72.4 |  | 69.2 |  | 68.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.8 |  | 70.7 | 63.9 | 64.7 | 66.2 | 67.6 |  | 74.6 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.9 |  | 49.4 | 41.8 | 36.1 | 38.1 | 33.4 |  | 53.6 |  | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.1 |  | 116.2 | 117.6 | 117.4 | 118.6 | 118.9 |  | 118.9 |  | 119.3
| INPUT | Kw | 1194kW |  | 1147 |  | 1175 | 1193 | 1176 | 1203 | 1204 |  | 1200 |  | 1202
COMPRESSOR | RUNNING TIME | Hr | NA |  |  |  |  | 49691.3 |  | 52127.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 |  | 59.2 | 57.7 | 57.6 | 57.3 | 57.5 |  | 58.7 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 45 | 45 | 44.9 | 46 | 45 |  | 44.9 |  | 44.7
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.6 | 4.3 | 3.9 | 4.2 | 4.1 |  | 4.4 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 |  | 2.7 | 3.6 | 3.3 | 3.1 | 3 |  | 3.3 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 0.5 | 0 | 2.2 | 0.7 | 1.3 | 1.5 | 1 | 0 | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 628.88 |  | 631.92 | 641.9 | 638 | 707.1 | 634.64 |  | 637.68 |  | 646.72
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.5 | 13.1 | 13.4 | 13.2 | 13.5 |  | 13.4 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.4 |  | 4.9 | 4.3 | 4.6 | 4.6 | 4 |  | 4.4 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.1 | 0 | 8.6 | 8.8 | 8.8 | 8.6 | 9.5 | 0 | 9 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6608.3233 | 0 | 6275.418 | 6522.7714 | 6483.1409 | 7022.0092 | 6961.9861 | 0 | 6627.1594 | 0 | 6422.3926
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 | 0.82 | 0.84 | 0.82 | 0.84 |  | 0.82 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.2 |  | 36.6 | 35.8 | 36.5 | 35.8 | 36.6 |  | 35.8 |  | 36.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.7 |  | 37.5 | 36.5 | 37.2 | 36.4 | 37.1 |  | 36.3 |  | 37.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.3 | 1 | 3.6 | 2.1 | 2.8 | 2.3 | 3 | 0 | 2.3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.2 |  | 29 | 28.8 | 29 | 28.8 | 28.9 |  | 29 |  | 29.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.4 |  | 33.9 | 34.4 | 34.4 | 34.1 | 34.1 |  | 34 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 0 | 4.9 | 5.6 | 5.4 | 5.3 | 5.2 | 0 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1301.16 |  | 1300.6 | 1305.1 | 1306.76 | 1302.2 | 1288.98 |  | 1291.22 |  | 1297.94
| HEAT CAPACITY | kW | 8226.9 | 0 | 7812.97 | 0 | 7359.0531 | 8439.4457 | 8148.388 | 7969.5843 | 7739.8337 | 0 | 7455.0808 | 0 | 7793.6351
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.46 | 0.47 | 0.46 | 0.46 |  | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 |  | 19.8 | 19.5 | 19.9 | 19.5 | 19.8 |  | 19.5 |  | 20.3
| LIQUID LEVEL | mm | mm |  | 189.3 |  | 127 | 203.2 | 209.5 | 212 | 216 |  | 160.5 |  | 201.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.77 |  | 5.59 | 5.44 | 5.65 | 5.27 | 5.72 |  | 5.63 |  | 5.22
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 11
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-11
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 72.1 |  | 81.4 | 72.8 | 73.8 | 74.5 | 75.3 |  | 75.6 |  | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.9 |  | 77.9 | 69.1 | 70.1 | 72.2 | 72 |  | 70.4 |  | 70.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69 |  | 69.7 | 63.8 | 64.9 | 67.8 | 68.2 |  | 75 |  | 73.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 38.5 |  | 57.1 | 41.4 | 41.3 | 38.1 | 35.6 |  | 58 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.1 |  | 118.4 | 115.3 | 115.7 | 116.8 | 117.6 |  | 117.7 |  | 118.6
| INPUT | Kw | 1194kW |  | 1150 |  | 1197 | 1172 | 1175 | 1190 | 1194 |  | 1194 |  | 1200
COMPRESSOR | RUNNING TIME | Hr | NA |  |  |  |  | 49712.2 |  | 52150
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.3 | 57.6 | 57.7 | 57.3 | 57.5 |  | 58.7 |  | 59
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 | 0.59 | 0.58 | 0.52 | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 44.8 | 45 | 45.1 | 45 | 44.8 |  | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.22 | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.2 |  | 3.2 | 4 | 4 | 4 | 4 |  | 4.3 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.7 |  | 2.3 | 3.2 | 3.3 | 3 | 2.8 |  | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | 2.4 | 0.8 | 0.7 | 1.3 | 1.6 | 0 | 1.3 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 642.2 |  | 631.9 | 625.23 | 635.44 | 639.4 | 627.8 |  | 642.9 |  | 639.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.8 |  | 13.8 | 13.3 | 13.2 | 13.7 | 13.7 |  | 13.9 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 |  | 4.7 | 4 | 4 | 4.3 | 4.4 |  | 4.6 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.1 | 0 | 9.1 | 9.3 | 9.2 | 9.4 | 9.3 | 0 | 9.3 | 0 | 9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6748.291 | 0 | 6640.0577 | 6714.3637 | 6750.6328 | 6940.3695 | 6741.963 | 0 | 6904.1224 | 0 | 6645.0346
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 |  | 0.82 | 0.81 | 0.81 | 0.81 | 0.81 |  | 0.79 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.3 |  | 35.9 | 35.4 | 35.6 | 35.4 | 35.6 |  | 34.8 |  | 35.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.8 |  | 36.8 | 36.1 | 36.3 | 36 | 36.1 |  | 35.3 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.7 | 0 | 3.3 | 2.2 | 2.2 | 2.4 | 2.2 | 0 | 1.5 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.6 |  | 28.5 | 28.5 | 28.7 | 28.4 | 28.7 |  | 28.3 |  | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.1 |  | 33.5 | 33.9 | 34.1 | 33.6 | 33.9 |  | 33.8 |  | 33.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 5 | 5.4 | 5.4 | 5.2 | 5.2 | 0 | 5.5 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1296.1 |  | 1290.6 | 1297.2 | 1304.9 | 1296.4 | 1293.9 |  | 1291.9 |  | 1294.6
| HEAT CAPACITY | kW | 8226.9 | 0 | 8231.582 | 0 | 7451.5012 | 8088.776 | 8136.7898 | 7784.388 | 7769.3764 | 0 | 8204.9076 | 0 | 7923.0716
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 | 0.45 | 0.45 | 0.45 | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.5 |  | 18.7 | 19.1 | 19.3 | 19.2 | 19.2 |  | 19.6 |  | 19.6
| LIQUID LEVEL | mm | mm |  | 202.9 |  | 122.5 | 209.2 | 205.4 | 202.2 | 214.9 |  | 160.3 |  | 199
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.84 |  | 5.61 | 5.85 | 5.79 | 5.87 | 5.74 |  | 5.74 |  | 5.52
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 12
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-12
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 69.7 |  | 81.7 |  | 73.9 |  | 76 | 78.1 | 78 | 77.4 | 73.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.3 |  | 78.3 |  | 69.1 |  | 71.5 | 73.7 | 74 | 73.3 | 68.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.4 |  | 69.9 |  | 64.6 |  | 68.6 | 72.2 | 73.8 | 71.5 | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 38.8 |  | 57.3 |  | 41.6 |  | 36.2 | 56.7 | 56.1 | 44.5 | 45.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 115.4 |  | 117.9 |  | 115.8 |  | 117.2 | 119.2 | 119.1 | 120.4 | 116.3
| INPUT | Kw | 1194kW |  | 1123 |  | 1194 |  | 1167 |  | 1190 | 1220 | 1205 | 1228 | 1175
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50637.9 |  | 51605.7 |  | 49720.2 |  | 52158 | 51322.4 | 51167 | 51080.5 | 50975.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59.2 |  | 57.7 |  | 57.3 | 58.4 | 58.5 | 59.1 | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.48 |  | 0.58 |  | 0.52 | 0.48 | 0.48 | 0.5 | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 45 |  | 45 |  | 44.9 | 45.1 | 45 | 44.9 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 |  | 0.23 |  | 0.22 | 0.23 | 0.22 | 0.23 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.1 |  | 3 |  | 3.9 |  | 3.9 | 4.4 | 3.9 | 4.8 | 4.4
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.7 |  | 2.1 |  | 3.1 |  | 2.8 | 3.6 | 2.9 | 3.8 | 3.3
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 0 | 2.5 | 0 | 0.8 | 0 | 1.4 | 1.2 | 1.3 | 1.2 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 653.4 |  | 635.9 |  | 638.1 |  | 626.4 | 722.9 | 635.6 | 692.5 | 636.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.8 |  | 13.6 |  | 13.1 |  | 13.7 | 13.4 | 13.7 | 13.2 | 13.1
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.6 |  | 3.9 |  | 4.2 | 4.8 | 4.2 | 5 | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.2 | 0 | 9 | 0 | 9.2 | 0 | 9.5 | 8.6 | 9.5 | 8.2 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6941.4319 | 0 | 6608.6605 | 0 | 6778.8915 | 0 | 6871.5935 | 7178.9145 | 6972.5173 | 6557.1594 | 6321.8938
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 |  | 0.82 |  | 0.8 |  | 0.8 | 0.8 | 0.8 | 0.82 | 0.8
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 34.9 |  | 35.5 |  | 35.3 |  | 35.3 | 34.9 | 34.5 | 35.7 | 35
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.4 |  | 36.4 |  | 36 |  | 35.8 | 35.6 | 35.1 | 36.5 | 35.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.6 | 0 | 3.2 | 0 | 2.2 | 0 | 2.3 | 1.7 | 1.6 | 2.5 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.3 |  | 28.2 |  | 28.4 |  | 28.2 | 28.4 | 28.1 | 28.4 | 28
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.8 |  | 33.2 |  | 33.8 |  | 33.5 | 33.9 | 33.5 | 34 | 33.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 5 | 0 | 5.4 | 0 | 5.3 | 5.5 | 5.4 | 5.6 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1300.3 |  | 1301.9 |  | 1300.9 |  | 1297.1 | 1283.7 | 1288.4 | 1293.7 | 1299.8
| HEAT CAPACITY | kW | 8226.9 | 0 | 8258.2564 | 0 | 7516.7436 | 0 | 8111.8476 | 0 | 7938.3718 | 8152.8291 | 8033.903 | 8365.7275 | 8104.9885
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.44 |  | 0.45 |  | 0.45 | 0.45 | 0.44 | 0.46 | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.4 |  | 18.8 |  | 19.1 |  | 19.2 | 19 | 18.5 | 19.8 | 19.4
| LIQUID LEVEL | mm | mm |  | 202.8 |  | 117 |  | 202.7 |  | 223.6 | 149.7 | 167.9 | 204.1 | 197.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 6 |  | 5.6 |  | 5.84 |  | 5.89 | 5.19 | 5.8 | 4.96 | 5.49
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 13
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-13
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 70 | 70 |  | 78.5 |  | 74.3 | 77.1 | 76.4 |  | 76.1 |  | 72.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.1 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 63.7 | 63.6 |  | 73.8 |  | 69 | 73.1 | 70.9 |  | 73.4 |  | 65.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 68.3 | 68.9 |  | 70.3 |  | 64.6 | 67.2 | 67.7 |  | 73.5 |  | 72.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 33.4 | 38 |  | 52.1 |  | 40.1 | 32.9 | 33.7 |  | 53.2 |  | 44.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 114.9 | 116.4 |  | 118 |  | 116.5 | 120.1 | 119.1 |  | 120.3 |  | 116.8
| INPUT | Kw | 1194kW | 1134 | 1132 |  | 1186 |  | 1176 | 1220 | 1202 |  | 1214 |  | 1175
COMPRESSOR | RUNNING TIME | Hr | NA | 50788.2 | 50777.1 |  | 51711.3 |  | 49729 | 52177.2 | 52166.1 |  | 51336.3 |  | 51087.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.2 |  | 59.3 |  | 57.7 | 57.5 | 57.6 |  | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.53 |  | 0.49 |  | 0.59 | 0.53 | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 44.9 |  | 44.9 |  | 45 | 44.9 | 44.8 |  | 44.9 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.1 | 4.3 |  | 3.6 |  | 4.2 | 4.2 | 4.1 |  | 4.3 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C | 3.9 | 4 |  | 2.7 |  | 3.3 | 3.2 | 3 |  | 3.2 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0.7 | 0.8 | 0 | 2.5 | 0 | 0.7 | 1.2 | 1.3 | 0 | 1.4 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 640.3 | 666.8 |  | 670.4 |  | 631.5 | 640.3 | 640 |  | 653 |  | 634.1
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.5 | 13.7 |  | 13.7 |  | 13.1 | 13.6 | 13.6 |  | 13.8 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.6 | 4.8 |  | 5.2 |  | 4 | 4.4 | 4.3 |  | 4.6 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.9 | 8.9 | 0 | 8.5 | 0 | 9.1 | 9.2 | 9.3 | 0 | 9.2 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 6580.4503 | 6852.7945 | 0 | 6580.1386 | 0 | 6635.8545 | 6802.2633 | 6872.9792 | 0 | 6937.1824 | 0 | 6443.5104
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.83 | 0.81 |  | 0.84 |  | 0.83 | 0.83 | 0.82 |  | 0.86 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.4 | 35.7 |  | 36.2 |  | 36 | 37.2 | 36.1 |  | 35.4 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C | 37 | 36.2 |  | 37.2 |  | 36.8 | 37.6 | 36.6 |  | 35.8 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.6 | 1.7 | 1 | 3.3 | 0 | 2.2 | 2.2 | 2.2 | 0 | 1.5 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 30.1 | 29.2 |  | 29 |  | 29.2 | 30.1 | 29 |  | 28.9 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 35.4 | 34.5 |  | 33.9 |  | 34.6 | 35.4 | 34.4 |  | 34.3 |  | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.3 | 5.3 | 0 | 4.9 | 0 | 5.4 | 5.3 | 5.4 | 0 | 5.4 | 0 | 5.1
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1292.9 | 1297.2 |  | 1300.1 |  | 1295.2 | 1306.4 | 1299.7 |  | 1290.5 |  | 1297.1
| HEAT CAPACITY | kW | 8226.9 | 7912.6674 | 7938.9838 | 0 | 7356.224 | 0 | 8076.3048 | 7995.2887 | 8104.3649 | 0 | 8046.9977 | 0 | 7638.8106
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.48 | 0.47 |  | 0.46 |  | 0.46 | 0.47 | 0.46 |  | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 20.4 | 20 |  | 19.6 |  | 19.7 | 20.3 | 19.8 |  | 19.2 |  | 20.1
| LIQUID LEVEL | mm | mm | 203.3 | 207 |  | 126.7 |  | 202.7 | 216.7 | 216.2 |  | 160.2 |  | 193.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.86 | 5.86 |  | 5.29 |  | 5.73 | 5.54 | 5.65 |  | 5.56 |  | 5.49
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 14
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-14
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 72.1 | 71.2 |  | 77.1 |  | 75.2 | 75.4 | 76 |  | 76.7 |  | 73.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 66.9 | 64.7 |  | 72.7 |  | 70.9 | 70.4 | 73.1 |  | 72.1 |  | 67.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 70.1 | 69.9 |  | 72.1 |  | 65.2 | 68.7 | 67.1 |  | 74.6 |  | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 37.6 | 35.4 |  | 51.1 |  | 39.7 | 34.5 | 36.5 |  | 55.7 |  | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 117.6 | 117.4 |  | 117.8 |  | 118.7 | 117.1 | 119.4 |  | 120.4 |  | 117.6
| INPUT | Kw | 1194kW | 1147 | 1156 |  | 1191 |  | 1209 | 1192 | 1208 |  | 1219 |  | 1189
COMPRESSOR | RUNNING TIME | Hr | NA | 50804.5 | 50798.7 |  | 51720.7 |  | 49738.5 | 52194.9 | 52189.9 |  | 51345.9 |  | 51096.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.4 | 58.1 |  | 59.5 |  | 57.9 | 57.5 | 57.4 |  | 58 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.59 | 0.52 | 0.52 |  | 0.53 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 45 |  | 44.8 |  | 44.9 | 44.8 | 45.1 |  | 44.6 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.24 |  | 0.22 |  | 0.23 | 0.22 | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.1 | 4.4 |  | 4 |  | 4.2 | 4.1 | 4.1 |  | 4.5 |  | 4.3
| SATURATION TEMPERATURE | CELCIUS | C | 3.3 | 4 |  | 2.9 |  | 3.4 | 2.8 | 2.9 |  | 3.1 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 1 | 0.6 | 0 | 2.1 | 0 | 1.1 | 1.1 | 1.1 | 0 | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 644.48 | 640.64 |  | 650.88 |  | 631.12 | 623.68 | 627.36 |  | 637.92 |  | 633.36
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.2 | 13.5 |  | 13.6 |  | 13.5 | 13.6 | 13.6 |  | 13.2 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 4.6 |  | 5 |  | 4.5 | 3.9 | 4 |  | 4.2 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.9 | 8.9 | 0 | 8.6 | 0 | 9 | 9.7 | 9.6 | 0 | 9 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 6623.4088 | 6583.9446 | 0 | 6463.7044 | 0 | 6558.9838 | 6985.7921 | 6954.5681 | 0 | 6629.6536 | 0 | 6362.8545
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.79 | 0.82 |  | 0.84 |  | 0.84 | 0.79 | 0.83 |  | 0.81 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.6 | 36.2 |  | 36.7 |  | 36.5 | 36 | 36.6 |  | 35.9 |  | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C | 35.1 | 36.5 |  | 37.4 |  | 37.1 | 35.4 | 36.9 |  | 36.1 |  | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.5 | 2.4 | 1 | 3.8 | 0 | 2.8 | 2.9 | 2.9 | 0 | 2.2 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.5 | 28.9 |  | 28.7 |  | 28.8 | 27.1 | 28.7 |  | 28.8 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 32.6 | 34.1 |  | 33.6 |  | 34.3 | 32.5 | 34 |  | 33.9 |  | 34.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.1 | 5.2 | 0 | 4.9 | 0 | 5.5 | 5.4 | 5.3 | 0 | 5.1 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1287.86 | 1292.2 |  | 1303.54 |  | 1287.58 | 1299.2 | 1297.94 |  | 1287.16 |  | 1299.62
| HEAT CAPACITY | kW | 8226.9 | 7584.3949 | 7759.1686 | 0 | 7375.6882 | 0 | 8177.4711 | 8101.2471 | 7943.5127 | 0 | 7580.2725 | 0 | 7803.7229
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.47 |  | 0.47 |  | 0.46 | 0.46 | 0.47 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.7 | 20.1 |  | 19.8 |  | 19.7 | 19.6 | 19.8 |  | 19.6 |  | 20.2
| LIQUID LEVEL | mm | mm | 197.5 | 201 |  | 133 |  | 204.8 | 219.1 | 204 |  | 151.3 |  | 192.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.93 | 5.93 |  | 5.23 |  | 5.54 | 5.7 | 5.78 |  | 5.63 |  | 5.38
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 15
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-15
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.6 | 80.4 | 77.4 |  | 74.3 | 71.8 | 75.7 |  | 74.3 |  | 73.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0 | 0 |  | 0 | 0.1 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.9 | 76.4 | 72.1 |  | 68.4 | 68.7 | 72.4 |  | 69.2 |  | 68.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.8 | 68 | 70.7 |  | 64.7 | 65.5 | 67.6 |  | 74.6 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.9 | 51.8 | 49.4 |  | 36.1 | 31.2 | 33.4 |  | 53.6 |  | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.1 | 117.2 | 116.2 |  | 117.4 | 114.4 | 118.9 |  | 118.9 |  | 119.3
| INPUT | Kw | 1194kW |  | 1147 | 1190 | 1175 |  | 1176 | 1164 | 1204 |  | 1200 |  | 1202
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50808.9 | 51740.4 | 51731.1 |  | 49763.1 | 52209.7 | 52200.4 |  | 51368.8 |  | 51106.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 | 59.2 | 59.2 |  | 57.6 | 57.5 | 57.5 |  | 58.7 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.49 | 0.5 |  | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 | 44.9 | 45 |  | 44.9 | 45 | 45 |  | 44.9 |  | 44.7
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.22 |  | 0.23 | 0.22 | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 | 3.1 | 3.6 |  | 3.9 | 3.7 | 4.1 |  | 4.4 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 | 2.1 | 2.7 |  | 3.3 | 2.6 | 3 |  | 3.3 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 0.5 | 2.7 | 2.2 | 0 | 1.3 | 1.3 | 1 | 0 | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 628.88 | 677.4 | 631.92 |  | 638 | 629.9 | 634.64 |  | 637.68 |  | 646.72
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 | 13 | 13.5 |  | 13.4 | 12.8 | 13.5 |  | 13.4 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.4 | 4.8 | 4.9 |  | 4.6 | 3.9 | 4 |  | 4.4 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.1 | 8.2 | 8.6 | 0 | 8.8 | 8.9 | 9.5 | 0 | 9 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6608.3233 | 6414.1801 | 6275.418 | 0 | 6483.1409 | 6473.5681 | 6961.9861 | 0 | 6627.1594 | 0 | 6422.3926
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.84 | 0.85 |  | 0.84 | 0.82 | 0.84 |  | 0.82 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.2 | 36.5 | 36.6 |  | 36.5 | 36.2 | 36.6 |  | 35.8 |  | 36.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.7 | 37.4 | 37.5 |  | 37.2 | 36.6 | 37.1 |  | 36.3 |  | 37.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.3 | 1 | 3.6 | 0 | 2.8 | 2.6 | 3 | 0 | 2.3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.2 | 28.8 | 29 |  | 29 | 28.8 | 28.9 |  | 29 |  | 29.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.4 | 33.7 | 33.9 |  | 34.4 | 34 | 34.1 |  | 34 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 4.9 | 4.9 | 0 | 5.4 | 5.2 | 5.2 | 0 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1301.16 | 1285.2 | 1300.6 |  | 1306.76 | 1290 | 1288.98 |  | 1291.22 |  | 1297.94
| HEAT CAPACITY | kW | 8226.9 | 0 | 7812.97 | 7271.9169 | 7359.0531 | 0 | 8148.388 | 7745.9584 | 7739.8337 | 0 | 7455.0808 | 0 | 7793.6351
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.45 | 0.46 |  | 0.47 | 0.46 | 0.46 |  | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 | 19 | 19.8 |  | 19.9 | 19.5 | 19.8 |  | 19.5 |  | 20.3
| LIQUID LEVEL | mm | mm |  | 189.3 | 129.9 | 127 |  | 209.5 | 200.7 | 216 |  | 160.5 |  | 201.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.77 | 5.13 | 5.59 |  | 5.65 | 5.7 | 5.72 |  | 5.63 |  | 5.22
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 16
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-16
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 74.6 | 70.3 |  | 83 |  | 68.5 |  | 79.1 | 78.1 | 73.5 |  | 74.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.1 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.7 | 64.6 |  | 79.9 |  | 64.4 |  | 74.5 | 73.4 | 68.7 |  | 59.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.2 | 69.5 |  | 70.3 |  | 64.8 |  | 68.4 | 75.3 | 72.8 |  | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 42 | 42 |  | 57.1 |  | 41.3 |  | 37.4 | 50.3 | 58.1 |  | 44.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 117 | 115.2 |  | 118.1 |  | 111.7 |  | 116.9 | 118 | 113.8 |  | 116.7
| INPUT | Kw | 1194kW | 1153 | 1126 |  | 1189 |  | 1131 |  | 1195 | 1203 | 1160 |  | 1191
COMPRESSOR | RUNNING TIME | Hr | NA | 50827.3 | 50819.4 |  | 51756.4 |  | 49773.9 |  | 52225.7 | 51387.4 | 51379.5 |  | 51117.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 58.2 |  | 59.4 |  | 57.9 |  | 57.3 | 58.5 | 58.4 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  | 0.58 |  | 0.64 | 0.47 | 0.47 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 44.2 |  | 45.1 |  | 45 |  | 45 | 44.8 | 45.1 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.25 |  | 0.21 |  | 0.22 |  | 0.21 | 0.23 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4 | 4 |  | 2.7 |  | 4.2 |  | 3.4 | 4.1 | 3.7 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 3.5 | 3.5 |  | 4.9 |  | 3.3 |  | 2.4 | 3.2 | 2.2 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0.9 | 0.8 | 0 | -0.3 | 0 | 1 | 0 | 1.5 | 1 | 1.6 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 670.88 | 634.8 |  | 645.2 |  | 633.5 |  | 630 | 664.72 | 639.2 |  | 635.8
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.2 | 13.4 |  | 13.5 |  | 13.2 |  | 13.7 | 13.2 | 12.7 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.4 | 4.3 |  | 4.6 |  | 4.3 |  | 3.9 | 4.2 | 3.8 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.8 | 9.1 | 0 | 8.9 | 0 | 8.9 | 0 | 9.8 | 9 | 8.9 | 0 | 9
| CHILLING CAPACITY | kW | 7032.6kW | 6817.2564 | 6670.5312 | 0 | 6630.8083 | 0 | 6510.5658 | 0 | 7129.3303 | 6908.1755 | 6569.1455 | 0 | 6607.6212
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.73 |  | 0.81 |  | 0.79 |  | 0.79 | 0.79 | 0.77 |  | 0.8
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35 | 34.6 |  | 35.1 |  | 34.7 |  | 34.9 | 34.6 | 34 |  | 34.9
| SATURATED TEMEPRATURE | CELCIUS | C | 35.6 | 35 |  | 36.4 |  | 35.5 |  | 35.4 | 35.2 | 34.5 |  | 35.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.4 | 1.7 | 1 | 3.6 | 0 | 2.2 | 0 | 2.3 | 2.5 | 1.6 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.9 | 27.9 |  | 27.8 |  | 28 |  | 27.9 | 27.6 | 27.6 |  | 27.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.2 | 33.3 |  | 32.8 |  | 33.3 |  | 33.1 | 32.7 | 32.9 |  | 33.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.3 | 5.4 | 0 | 5 | 0 | 5.3 | 0 | 5.2 | 5.1 | 5.3 | 0 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1293.6 | 1292.6 |  | 1299.7 |  | 1301.7 |  | 1294.7 | 1298.5 | 1291 |  | 1296.4
| HEAT CAPACITY | kW | 8226.9 | 7916.9515 | 8060.0924 | 0 | 7504.0416 | 0 | 7966.5242 | 0 | 7774.1801 | 7647.0554 | 7901.0393 | 0 | 8233.4873
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.45 |  | 0.43 |  | 0.45 |  | 0.44 | 0.44 | 0.44 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.3 | 19.7 |  | 18.1 |  | 19.1 |  | 18.7 | 18.6 | 18.2 |  | 19.4
| LIQUID LEVEL | mm | mm | 197 | 200.6 |  | 119.6 |  | 199.1 |  | 209.5 | 154.1 | 158.6 |  | 198.4
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 6.03 | 6.15 |  | 5.64 |  | 5.87 |  | 5.9 | 5.77 | 5.88 |  | 5.45
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 17
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-17
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 67.8 |  | 76.4 | 74 | 73.6 | 77 | 74.3 |  | 76.7 |  | 74
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 62 |  | 71.2 | 69.4 | 67.6 | 74.7 | 69.8 |  | 72.1 |  | 69.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.5 |  | 70.6 | 64.8 | 63.5 | 67.2 | 67.9 |  | 74.6 |  | 74.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 35.4 |  | 50.7 | 41.5 | 37.4 | 35.8 | 35.6 |  | 55.7 |  | 41.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 113.8 |  | 114.9 | 115.6 | 115.2 | 117.2 | 115.7 |  | 120.4 |  | 117.6
| INPUT | Kw | 1194kW |  | 1123 |  | 1178 | 1172 | 1185 | 1202 | 1191 |  | 1219 |  | 1205
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50839.2 |  | 51764.2 | 49791.4 | 49782.1 | 52242.9 | 52233.7 |  | 51396.3 |  | 51126
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 58.9 | 57.5 | 57.9 | 57.2 | 57.4 |  | 58 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.53 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 |  | 45.1 | 44.9 | 44.8 | 45 | 45.1 |  | 44.6 |  | 45.2
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.2 |  | 3.5 | 4 | 4.1 | 3.7 | 4.1 |  | 4.5 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.7 | 3.2 | 3.4 | 2.8 | 2.9 |  | 3.1 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0 | 2.3 | 1.3 | 0.8 | 1.7 | 1.1 | 0 | 1.1 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 644.3 |  | 637.3 | 644.96 | 636.29 | 709.36 | 675.7 |  | 655.4 |  | 641.8
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.8 |  | 13.7 | 13.5 | 13.2 | 13.3 | 13.6 |  | 13.2 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 5 | 4.5 | 4.2 | 4.5 | 4 |  | 4.2 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.2 | 0 | 8.7 | 9 | 9 | 8.8 | 9.6 | 0 | 9 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6844.7575 | 0 | 6402.4365 | 6702.8176 | 6612.7136 | 7208.2771 | 7490.4388 | 0 | 6811.3164 | 0 | 6373.5335
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.84 | 0.82 | 0.83 | 0.83 | 0.83 |  | 0.81 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.8 |  | 36.4 | 35.4 | 36.3 | 35.4 | 36.6 |  | 35.9 |  | 36.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 37.3 | 36.5 | 37 | 36.6 | 36.9 |  | 36.1 |  | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.7 | 1 | 3.1 | 2.9 | 2.1 | 3.1 | 2.9 | 0 | 2.2 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.5 |  | 29.3 | 28.3 | 29.5 | 28.1 | 28.7 |  | 28.8 |  | 29.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.7 |  | 34.2 | 33.6 | 34.9 | 33.5 | 34 |  | 33.9 |  | 34.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 0 | 4.9 | 5.3 | 5.4 | 5.4 | 5.3 | 0 | 5.1 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1296.8 |  | 1300.5 | 1303.54 | 1299 | 1291.08 | 1298 |  | 1297.1 |  | 1297.6
| HEAT CAPACITY | kW | 8226.9 | 0 | 7786.7898 | 0 | 7358.4873 | 7977.7852 | 8100 | 8050.6143 | 7943.8799 | 0 | 7638.8106 | 0 | 8091.2702
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.45 | 0.46 | 0.45 | 0.47 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 |  | 19.6 | 19.2 | 19.6 | 19.6 | 19.8 |  | 19.6 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 196.6 |  | 129.5 | 209.6 | 205 | 207.3 | 204 |  | 151.3 |  | 197.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 6.05 |  | 5.45 | 5.84 | 5.68 | 5.81 | 5.78 |  | 5.63 |  | 5.27
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 18
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-18
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 67.6 |  | 76.1 | 73.2 | 74 |  | 75.8 | 77.9 | 72.4 |  | 73.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 61.8 |  | 71.7 | 68.7 | 69.4 |  | 73.7 | 72.7 | 76.3 |  | 68.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.5 |  | 70.9 | 65.3 | 63.2 |  | 67.3 | 74.7 | 67.8 |  | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.9 |  | 54.2 | 39.2 | 39.7 |  | 37.1 | 58.8 |  |  | 40.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 114 |  | 116.1 | 116.3 | 117.2 |  | 118.6 | 118.8 | 116 |  | 117.6
| INPUT | Kw | 1194kW |  | 1125 |  | 1171 | 1180 | 1180 |  | 1207 | 1203 | 1180 |  | 1193
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50849 |  | 51774.2 | 49810.3 | 49801.6 |  | 52258.1 | 51415.2 | 51406.5 |  | 51136.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.1 | 57.7 | 57.5 |  | 57.5 | 58.4 | 58.5 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.58 |  |  | 0.52 | 0.47 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.7 |  | 45.2 | 45 | 44 |  | 44.8 | 45.4 | 45 |  | 44.7
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.5 | 4.1 | 4.1 |  | 4.1 | 4.4 | 4.3 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.7 | 3.2 | 3 |  | 2.9 | 3.6 | 3.2 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 0 | 2.2 | 1.1 | 1.1 | 0 | 1.4 | 0.8 | 1.4 | 0 | 0.3
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 638.1 |  | 630.1 | 629.8 | 631.9 |  | 640.2 | 386.4 | 636.8 |  | 630.7
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.7 |  | 14 | 13.5 | 13.3 |  | 13.4 | 13.2 | 13.9 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 |  | 4.9 | 4.3 | 4.1 |  | 4.3 | 4.4 | 4.6 |  | 3.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9 | 0 | 9.1 | 9.2 | 9.2 | 0 | 9.1 | 8.8 | 9.3 | 0 | 9.5
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6631.5242 | 0 | 6621.1432 | 6690.7159 | 6713.0254 | 0 | 6727.2748 | 3926.4665 | 6838.6143 | 0 | 6918.7644
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.83 | 0.8 | 0.83 |  | 0.82 | 0.7 | 0.81 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.9 |  | 36.2 | 35.2 | 36.2 |  | 36.3 | 34.3 | 35.3 |  | 36.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.2 |  | 37.1 | 35.9 | 36.9 |  | 36.7 | 34.9 | 35.8 |  | 36.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.5 | 0 | 3.1 | 2.2 | 2.1 | 0 | 2.2 | 1.7 | 1.6 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.2 |  | 29.3 | 28.2 | 29.3 |  | 29.1 | 27.8 | 29 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.7 |  | 34 | 33.7 | 34.8 |  | 34.5 | 33.2 | 34.2 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 4.7 | 5.5 | 5.5 | 0 | 5.4 | 5.4 | 5.2 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1300.7 |  | 1296.9 | 1289.8 | 1293.6 |  | 1301.4 | 1302.1 | 1293.9 |  | 1298.3
| HEAT CAPACITY | kW | 8226.9 | 0 | 8260.7968 | 0 | 7038.6028 | 8191.5704 | 8215.7044 | 0 | 8114.9654 | 8119.3303 | 7769.3764 | 0 | 8095.6351
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.45 | 0.46 |  | 0.46 | 0.44 | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 |  | 19.4 | 19 | 19.8 |  | 19.5 | 18.6 | 19.6 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 199.5 |  | 121.3 | 204.5 | 202.4 |  | 208.8 | 163.1 | 170.6 |  | 204.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.96 |  | 5.66 | 5.75 | 5.77 |  | 5.68 | 5.54 | 5.87 |  | 5.37
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 19
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-19
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 71.9 | 72.1 |  | 81.4 |  | 73.8 |  | 75.3 | 77.4 | 75.6 |  | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.1 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 66 | 65.9 |  | 77.9 |  | 70.1 |  | 72 | 75.3 | 70.4 |  | 70.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 67.3 | 69 |  | 69.7 |  | 64.9 |  | 68.2 | 72.9 | 75 |  | 73.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 40.8 | 38.5 |  | 57.1 |  | 41.3 |  | 35.6 | 54.2 | 58 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118.6 | 117.1 |  | 118.4 |  | 115.7 |  | 117.6 | 121.3 | 117.7 |  | 118.6
| INPUT | Kw | 1194kW | 1164 | 1150 |  | 1197 |  | 1175 |  | 1194 | 1229 | 1194 |  | 1200
COMPRESSOR | RUNNING TIME | Hr | NA | 50867.9 | 50859 |  | 51787.5 |  | 49824 |  | 52268.3 | 51434.2 | 51241.7 |  | 51425
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.2 |  | 59.3 |  | 57.7 |  | 57.5 | 58.5 | 58.7 |  | 59
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 |  | 0.49 |  | 0.58 |  | 0.52 | 0.48 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 45.1 |  | 44.8 |  | 45.1 |  | 44.8 | 45.1 | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.21 |  | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.5 | 4.2 |  | 3.2 |  | 4 |  | 4 | 4.4 | 4.3 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C | 4 | 3.7 |  | 2.3 |  | 3.3 |  | 2.8 | 3.1 | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 1.1 | 1 | 0 | 2.4 | 0 | 0.7 | 0 | 1.6 | 1.6 | 1.3 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 697.9 | 642.2 |  | 631.9 |  | 635.44 |  | 627.8 | 687.9 | 642.9 |  | 639.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.6 | 13.8 |  | 13.8 |  | 13.2 |  | 13.7 | 13.7 | 13.9 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5.1 | 4.7 |  | 4.7 |  | 4 |  | 4.4 | 4.7 | 4.6 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.5 | 9.1 | 0 | 9.1 | 0 | 9.2 | 0 | 9.3 | 9 | 9.3 | 0 | 9
| CHILLING CAPACITY | kW | 7032.6kW | 6850.0577 | 6748.291 | 0 | 6640.0577 | 0 | 6750.6328 | 0 | 6741.963 | 7149.0762 | 6904.1224 | 0 | 6645.0346
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.8 |  | 0.82 |  | 0.81 |  | 0.81 | 0.8 | 0.79 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.7 | 35.3 |  | 35.9 |  | 35.6 |  | 35.6 | 35.2 | 34.8 |  | 35.5
| SATURATED TEMEPRATURE | CELCIUS | C | 36.2 | 35.8 |  | 36.8 |  | 36.3 |  | 36.1 | 35.3 | 35.3 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.6 | 1.7 | 0 | 3.3 | 0 | 2.2 | 0 | 2.2 | 1.1 | 1.5 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.9 | 28.6 |  | 28.5 |  | 28.7 |  | 28.7 | 28.7 | 28.3 |  | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.6 | 34.1 |  | 33.5 |  | 34.1 |  | 33.9 | 34.2 | 33.8 |  | 33.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.7 | 5.5 | 0 | 5 | 0 | 5.4 | 0 | 5.2 | 5.5 | 5.5 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1303.8 | 1296.1 |  | 1290.6 |  | 1304.9 |  | 1293.9 | 1299.9 | 1291.9 |  | 1294.6
| HEAT CAPACITY | kW | 8226.9 | 8581.5935 | 8231.582 | 0 | 7451.5012 | 0 | 8136.7898 | 0 | 7769.3764 | 8255.7159 | 8204.9076 | 0 | 7923.0716
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.46 |  | 0.45 |  | 0.45 |  | 0.46 | 0.45 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.9 | 19.5 |  | 18.7 |  | 19.3 |  | 19.2 | 19 | 19.6 |  | 19.6
| LIQUID LEVEL | mm | mm | 201.2 | 202.9 |  | 122.5 |  | 205.4 |  | 214.9 | 159.7 | 160.3 |  | 199
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.88 | 5.84 |  | 5.61 |  | 5.79 |  | 5.74 | 5.89 | 5.74 |  | 5.52
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 20
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-20
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.5 | 70 |  | 77.1 |  | 74.3 | 75.6 | 76.4 |  | 75.6 |  | 72.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0.1 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.4 | 63.6 |  | 72.7 |  | 69 | 73.3 | 70.9 |  | 70.4 |  | 65.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.6 | 68.9 |  | 72.1 |  | 64.6 | 68.9 | 67.7 |  | 75 |  | 72.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 41.7 | 38 |  | 51.1 |  | 40.1 | 36 | 33.7 |  | 58 |  | 44.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 117.5 | 116.4 |  | 117.8 |  | 116.5 | 116.1 | 119.1 |  | 117.7 |  | 116.8
| INPUT | Kw | 1194kW | 1150 | 1132 |  | 1191 |  | 1176 | 1180 | 1202 |  | 1194 |  | 1175
COMPRESSOR | RUNNING TIME | Hr | NA | 50887.8 | 50880.8 |  | 51798.5 |  | 49829 | 52288 | 52280 |  | 51236.7 |  | 51432
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.4 | 58.2 |  | 59.5 |  | 57.7 | 57.2 | 57.6 |  | 58.7 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 44.9 |  | 44.8 |  | 45 | 45.1 | 44.8 |  | 44.9 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.1 | 4.3 |  | 4 |  | 4.2 | 3.6 | 4.1 |  | 4.3 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C | 3.5 | 4 |  | 2.9 |  | 3.3 | 2.3 | 3 |  | 3.3 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 1.5 | 0.8 | 0 | 2.1 | 0 | 0.7 | 1.7 | 1.3 | 0 | 1.3 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 691 | 666.8 |  | 650.88 |  | 631.5 | 640.2 | 640 |  | 642.9 |  | 634.1
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.7 | 13.7 |  | 13.6 |  | 13.1 | 13.5 | 13.6 |  | 13.9 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5 | 4.8 |  | 5 |  | 4 | 4 | 4.3 |  | 4.6 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.7 | 8.9 | 0 | 8.6 | 0 | 9.1 | 9.5 | 9.3 | 0 | 9.3 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 6941.9169 | 6852.7945 | 0 | 6463.7044 | 0 | 6635.8545 | 7022.9792 | 6872.9792 | 0 | 6904.1224 | 0 | 6443.5104
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.81 |  | 0.84 |  | 0.83 | 0.8 | 0.82 |  | 0.79 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.3 | 35.7 |  | 36.7 |  | 36 | 34.6 | 36.1 |  | 34.8 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C | 34.9 | 36.2 |  | 37.4 |  | 36.8 | 35.2 | 36.6 |  | 35.3 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.6 | 1.7 | 0 | 3.8 | 0 | 2.2 | 2.3 | 2.2 | 0 | 1.5 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.6 | 29.2 |  | 28.7 |  | 29.2 | 27.7 | 29 |  | 28.3 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.3 | 34.5 |  | 33.6 |  | 34.6 | 32.9 | 34.4 |  | 33.8 |  | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.7 | 5.3 | 0 | 4.9 | 0 | 5.4 | 5.2 | 5.4 | 0 | 5.5 | 0 | 5.1
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1296.8 | 1297.2 |  | 1303.54 |  | 1295.2 | 1294 | 1299.7 |  | 1291.9 |  | 1297.1
| HEAT CAPACITY | kW | 8226.9 | 8535.5196 | 7938.9838 | 0 | 7375.6882 | 0 | 8076.3048 | 7769.9769 | 8104.3649 | 0 | 8204.9076 | 0 | 7638.8106
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.47 |  | 0.47 |  | 0.46 | 0.44 | 0.46 |  | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 18.9 | 20 |  | 19.8 |  | 19.7 | 18.5 | 19.8 |  | 19.6 |  | 20.1
| LIQUID LEVEL | mm | mm | 194.3 | 207 |  | 133 |  | 202.7 | 205.1 | 216.2 |  | 160.3 |  | 193.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.7 | 5.86 |  | 5.23 |  | 5.73 | 5.94 | 5.65 |  | 5.74 |  | 5.49
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 21
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-21
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71 |  | 81.1 | 72.8 | 71.8 |  | 77.4 | 78.1 | 77.2 |  | 74.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.1 |  | 77.7 | 69.1 | 67.5 |  | 74.8 | 73.7 | 71.9 |  | 68.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 68 |  | 69.9 | 63.8 | 63.6 |  | 67.1 | 72.2 | 73.9 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 40 |  | 51.6 | 41.4 | 37.9 |  | 38.8 | 56.7 | 54.5 |  | 44.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.2 |  | 117.9 | 115.3 | 116.2 |  | 120 | 119.2 | 118.8 |  | 118.3
| INPUT | Kw | 1194kW |  | 1153 |  | 1198 | 1172 | 1174 |  | 1218 | 1220 | 1207 |  | 1194
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50894.2 |  | 51802.2 | 49851 | 49841.7 |  | 52300.6 | 51466 | 51457.4 |  | 51164.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.3 | 57.6 | 57.5 |  | 57.2 | 58.4 | 58.7 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 | 0.59 | 0.59 |  | 0.52 | 0.48 | 0.47 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 45.1 | 45 | 44.8 |  | 45.1 | 45.1 | 44.9 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.22 | 0.23 |  | 0.22 | 0.23 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.7 |  | 3.7 | 4 | 4 |  | 4.1 | 4.4 | 4.6 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.1 |  | 2.9 | 3.2 | 3.2 |  | 3 | 3.6 | 3.5 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | 2.4 | 0.8 | 0.8 | 0 | 1.5 | 1.2 | 1.3 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 668.4 |  | 668.1 | 625.23 | 633.2 |  | 664.1 | 722.9 | 651.1 |  | 634
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.8 |  | 13.8 | 13.3 | 13.1 |  | 13.7 | 13.4 | 13.8 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5.1 |  | 5.3 | 4 | 4 |  | 4.5 | 4.8 | 4.8 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.7 | 0 | 8.5 | 9.3 | 9.1 | 0 | 9.2 | 8.6 | 9 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6714.873 | 0 | 6557.5635 | 6714.3637 | 6653.7182 | 0 | 7055.1039 | 7178.9145 | 6766.6282 | 0 | 6369.2841
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 |  | 0.83 | 0.81 | 0.82 |  | 0.82 | 0.8 | 0.86 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.8 |  | 36.2 | 35.4 | 36 |  | 36 | 34.9 | 35.4 |  | 36
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.2 |  | 37.1 | 36.1 | 36.7 |  | 36.5 | 35.6 | 35.8 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.6 | 1 | 3.1 | 2.2 | 2.1 | 0 | 2.2 | 1.7 | 1.5 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29 |  | 29 | 28.5 | 29.1 |  | 28.9 | 28.4 | 28.8 |  | 28.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.6 |  | 34 | 33.9 | 34.6 |  | 34.3 | 33.9 | 34.3 |  | 34.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.6 | 0 | 5 | 5.4 | 5.5 | 0 | 5.4 | 5.5 | 5.5 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1300.5 |  | 1302.6 | 1297.2 | 1296.3 |  | 1300 | 1283.7 | 1288.6 |  | 1293.7
| HEAT CAPACITY | kW | 8226.9 | 0 | 8409.6998 | 0 | 7520.7852 | 8088.776 | 8232.8522 | 0 | 8106.2356 | 8152.8291 | 8183.9492 | 0 | 7917.5635
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 | 0.45 | 0.46 |  | 0.46 | 0.45 | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 |  | 19.4 | 19.1 | 19.6 |  | 19.6 | 19 | 19.2 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 200.4 |  | 123.2 | 209.2 | 203.6 |  | 205.6 | 149.7 | 165.1 |  | 197.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.64 |  | 5.26 | 5.85 | 5.73 |  | 5.7 | 5.19 | 5.54 |  | 5.38
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 22
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-22
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 74.6 | 73.4 |  | 80.1 |  | 73.8 | 71.8 | 77.6 |  | 76.6 |  | 73.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.8 |  | 0 |  | 0 | 0.1 | 0.1 |  | 0.2 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.7 | 67.8 |  | 76.2 |  | 69.8 | 68.7 | 73.3 |  | 72.1 |  | 68.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.2 | 68.7 |  | 69.7 |  | 64.7 | 65.5 | 68.7 |  | 74.4 |  | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 42 | 39.1 |  | 54.6 |  | 38.8 | 31.2 | 38.1 |  | 42 |  | 46.3
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 117 | 118.8 |  | 117.5 |  | 116.1 | 114.4 | 119.4 |  | 119.4 |  | 118.3
| INPUT | Kw | 1194kW | 1153 | 1162 |  | 1194 |  | 1189 | 1164 | 1213 |  | 1208 |  | 1199
COMPRESSOR | RUNNING TIME | Hr | NA | 50912.6 | 50903.6 |  | 51811.5 |  | 49859.3 | 52315.6 | 52309.6 |  | 51478.5 |  | 51173.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 58.2 |  | 59.5 |  | 57.8 | 57.5 | 57.5 |  | 58.6 |  | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  | 0.58 | 0.52 | 0.52 |  | 0.47 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 45.1 |  | 44.8 |  | 44.7 | 45 | 44.9 |  | 44.9 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.23 | 0.22 | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4 | 4.1 |  | 3.5 |  | 4.2 | 3.7 | 4.2 |  | 4.4 |  | 5
| SATURATION TEMPERATURE | CELCIUS | C | 3.5 | 3.5 |  | 2.4 |  | 3.2 | 2.6 | 2.6 |  | 3.1 |  | 3.5
| APPROACH TEMP | CELCIUS | C | 0.9 | 0.8 | 0 | 2.3 | 0 | 1.3 | 1.3 | 1 | 0 | 1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 670.88 | 656.16 |  | 660.64 |  | 627.84 | 629.9 | 641.92 |  | 640.16 |  | 647.2
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.2 | 13.2 |  | 13.3 |  | 13.5 | 12.8 | 13 |  | 13.3 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.4 | 4.3 |  | 4.7 |  | 4.5 | 3.9 | 3.6 |  | 4.1 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.8 | 8.9 | 0 | 8.6 | 0 | 9 | 8.9 | 9.4 | 0 | 9.2 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 6817.2564 | 6743.4457 | 0 | 6560.6282 | 0 | 6524.8961 | 6473.5681 | 6967.7229 | 0 | 6800.776 | 0 | 6501.8938
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.8 |  | 0.82 |  | 0.81 | 0.82 | 0.81 |  | 0.79 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35 | 35.2 |  | 35.8 |  | 35.5 | 36.2 | 35.6 |  | 34.9 |  | 35.6
| SATURATED TEMEPRATURE | CELCIUS | C | 35.6 | 35.7 |  | 36.6 |  | 36.2 | 36.6 | 35.9 |  | 35.3 |  | 36.1
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.4 | 2.4 | 1 | 3.7 | 0 | 2.9 | 2.6 | 3 | 0 | 2.4 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.9 | 28 |  | 27.9 |  | 27.9 | 28.8 | 27.8 |  | 27.8 |  | 28
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.2 | 33.3 |  | 32.9 |  | 33.3 | 34 | 32.9 |  | 32.9 |  | 33.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.3 | 5.3 | 0 | 5 | 0 | 5.4 | 5.2 | 5.1 | 0 | 5.1 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1293.6 | 1301.72 |  | 1299.2 |  | 1295.42 | 1290 | 1296.26 |  | 1288.28 |  | 1299.62
| HEAT CAPACITY | kW | 8226.9 | 7916.9515 | 7966.6467 | 0 | 7501.1547 | 0 | 8077.6767 | 7745.9584 | 7633.8637 | 0 | 7586.8684 | 0 | 7953.7945
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.46 |  | 0.45 |  | 0.46 | 0.46 | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.3 | 19.7 |  | 18.9 |  | 19.1 | 19.5 | 19.4 |  | 18.7 |  | 19.9
| LIQUID LEVEL | mm | mm | 197 | 208.4 |  | 132.8 |  | 200.1 | 200.7 | 212 |  | 161.2 |  | 202
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 6.03 | 5.67 |  | 5.39 |  | 5.74 | 5.7 | 5.58 |  | 5.54 |  | 5.31
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 23
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-23
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 67.8 |  | 76.4 | 73.4 | 73.6 |  | 74.3 | 79.3 | 76.7 |  | 74
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 62 |  | 71.2 | 70.1 | 67.6 |  | 69.8 | 74.6 | 72.1 |  | 69.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.5 |  | 70.6 | 64.3 | 63.5 |  | 67.9 | 74 | 74.6 |  | 74.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 35.4 |  | 50.7 | 37.3 | 37.4 |  | 35.6 | 53.1 | 55.7 |  | 41.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 113.8 |  | 114.9 | 117.4 | 115.2 |  | 115.7 | 121.9 | 120.4 |  | 117.6
| INPUT | Kw | 1194kW |  | 1123 |  | 1178 | 1184 | 1185 |  | 1191 | 1238 | 1219 |  | 1205
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50920.4 |  | 51820.7 | 49879.7 | 49868.7 |  | 52327.5 | 51498.7 | 51487.8 |  | 51182.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 58.9 | 57.6 | 57.9 |  | 57.4 | 58.6 | 58 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.52 | 0.48 | 0.53 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 |  | 45.1 | 45 | 44.8 |  | 45.1 | 45.1 | 44.6 |  | 45.2
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.22 | 0.23 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.2 |  | 3.5 | 4 | 4.1 |  | 4.1 | 4.6 | 4.5 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.7 | 3.4 | 3.4 |  | 2.9 | 3.5 | 3.1 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | 1.8 | 0.7 | 1.1 | 0 | 0.9 | 1.3 | 1.3 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 655.28 |  | 629.04 | 625 | 629.92 |  | 633.28 | 689.3 | 635.68 |  | 637.36
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.5 | 13.3 | 13.6 |  | 13.3 | 13.8 | 13.5 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 |  | 4.5 | 4.1 | 4.5 |  | 3.8 | 4.8 | 4.4 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.7 | 0 | 9 | 9.2 | 9.1 | 0 | 9.5 | 9 | 9.1 | 0 | 8.8
|  | kW | 7032.6kW | 0 | 6583.067 | 0 | 6537.3672 | 6639.7229 | 6619.2517 | 0 | 6947.067 | 7163.6259 | 6679.7783 | 0 | 6476.6374
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.8 | 0.84 | 0.82 |  | 0.81 | 0.81 | 0.79 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.8 |  | 36.4 | 36.5 | 36.3 |  | 36.6 | 35.8 | 35.9 |  | 36.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.6 |  | 35.6 | 37.2 | 36.2 |  | 36.1 | 36.3 | 35.4 |  | 36.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 3.7 | 1 | 2.3 | 2.1 | 2.8 | 0 | 3.1 | 1.6 | 2.4 | 0 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.9 |  | 28.2 | 29.7 | 28 |  | 27.7 | 29.3 | 27.9 |  | 28.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 32.9 |  | 33.3 | 35.1 | 33.4 |  | 33 | 34.7 | 33 |  | 33.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5 | 0 | 5.1 | 5.4 | 5.4 | 0 | 5.3 | 5.4 | 5.1 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1293.88 |  | 1298.5 | 1299.8 | 1303.26 |  | 1292.06 | 1297.1 | 1283.66 |  | 1296.12
| HEAT CAPACITY | kW | 8226.9 | 0 | 7470.4388 | 0 | 7647.0554 | 8104.9885 | 8126.5635 | 0 | 7907.5266 | 8088.1524 | 7559.6605 | 0 | 7782.7067
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.46 | 0.46 |  | 0.47 | 0.46 | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 |  | 19.6 | 19.8 | 19.6 |  | 19.8 | 19.5 | 19.6 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 196.6 |  | 129.5 | 203.5 | 205 |  | 204 | 165.8 | 151.3 |  | 197.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 6.05 |  | 5.45 | 5.71 | 5.68 |  | 5.78 | 5.35 | 5.63 |  | 5.27
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 24
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-24
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.4 | 69.2 |  | 78 |  | 74 | 76.1 | 77.3 |  | 75.2 |  | 73.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.6 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.3 | 63 |  | 73.5 |  | 69.5 | 72.5 | 72.4. |  | 69.7 |  | 68.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 67.8 | 69.5 |  | 71.1 |  | 64.3 | 66.6 | 67.8 |  | 74.4 |  | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 37.9 | 39.1 |  | 54.6 |  | 40 | 36.8 | 34.1 |  | 56.1 |  | 43
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 119.4 | 114.7 |  | 116.3 |  | 115.2 | 119.4 | 117.7 |  | 116.7 |  | 117.6
| INPUT | Kw | 1194kW | 1163 | 1145 |  | 1188 |  | 1186 | 1208 | 1208 |  | 1195 |  | 1202
COMPRESSOR | RUNNING TIME | Hr | NA | 50939.6 | 50930 |  | 51830.6 |  | 49891.3 | 52347.1 | 52337.4 |  | 51509.5 |  | 51191.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.1 |  | 59.1 |  | 57.9 | 57.3 | 57.4 |  | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.5 |  | 0.59 | 0.52 | 0.52 |  | 0.47 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.2 | 44.9 |  | 45 |  | 45 | 44.9 | 45 |  | 45.1 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.24 | 0.25 |  | 0.22 |  | 0.22 | 0.23 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.1 | 4.5 |  | 4.3 |  | 4.2 | 4.2 | 3.9 |  | 4.2 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C | 4 | 3.9 |  | 3.5 |  | 3.3 | 3.5 | 2.9 |  | 3.3 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0.8 | 0.7 | 0 | 1.3 | 0 | 1 | 1.1 | 0.9 | 0 | 1 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 698.24 | 634.6 |  | 650.2 |  | 630.3 | 684.64 | 625.8 |  | 637.1 |  | 645
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.2 | 13.5 |  | 13.4 |  | 13.5 | 13.6 | 13.5 |  | 13.4 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.8 | 4.6 |  | 4.8 |  | 4.3 | 4.6 | 3.8 |  | 4.3 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.4 | 8.9 | 0 | 8.6 | 0 | 9.2 | 9 | 9.7 | 0 | 9.1 | 0 | 8.8
|  | kW | 7032.6kW | 6772.7667 | 6521.8707 | 0 | 6456.9515 | 0 | 6696.0277 | 7115.1963 | 7009.5381 | 0 | 6694.6998 | 0 | 6554.2725
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.81 |  | 0.84 |  | 0.88 | 0.83 | 0.84 |  | 0.8 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.4 | 36 |  | 36.3 |  | 36.2 | 35.9 | 36.3 |  | 35.4 |  | 36
| SATURATED TEMEPRATURE | CELCIUS | C | 36.4 | 36.8 |  | 37.3 |  | 36.9 | 36.8 | 36.8 |  | 35.9 |  | 36.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.4 | 2.1 | 1 | 3.3 | 0 | 2.1 | 3 | 2.4 | 0 | 1.6 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.5 | 29.3 |  | 29.3 |  | 29.1 | 28.4 | 29.3 |  | 29 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34 | 34.7 |  | 34 |  | 34.8 | 33.8 | 34.4 |  | 34.3 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.4 | 0 | 4.7 | 0 | 5.7 | 5.4 | 5.1 | 0 | 5.3 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1292.34 | 1297.6 |  | 1288.2 |  | 1296.5 | 1296.12 | 1298.9 |  | 1288.9 |  | 1296.9
| HEAT CAPACITY | kW | 8226.9 | 8207.7021 | 8091.2702 | 0 | 6991.3857 | 0 | 8533.545 | 8082.0416 | 7649.4111 | 0 | 7888.1871 | 0 | 8086.9053
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.47 |  | 0.4 |  | 0.46 | 0.46 | 0.46 |  | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.5 | 20.1 |  | 19.4 |  | 19.6 | 19.6 | 19.7 |  | 19.2 |  | 20
| LIQUID LEVEL | mm | mm | 203.5 | 197.8 |  | 120.8 |  | 204.1 | 222.9 | 214.6 |  | 164.8 |  | 197.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.45 | 5.87 |  | 5.49 |  | 5.69 | 5.42 | 5.82 |  | 5.71 |  | 5.33
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 25
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-25
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 69.4 |  | 77.7 | 74.9 | 74.3 |  | 76.1 |  | 72.4 | 74.3 | 73.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.5 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.7 |  | 72.9 | 69.8 | 69.2 |  | 72.5 |  | 76.3 | 69.7 | 68.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.3 |  | 70.7 | 36.2 | 64.4 |  | 67.5 |  | 67.8 | 73.4 | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.5 |  | 53.1 | 64.2 | 39.6 |  | 34.6 |  | 52.1 | 40.9 | 40.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 116.4 |  | 117.5 | 117.8 | 117.1 |  | 118.6 |  | 116 | 118 | 117.6
| INPUT | Kw | 1194kW |  | 1132 |  | 1181 | 1194 | 1180 |  | 1207 |  | 1180 | 1204 | 1193
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50948.9 |  | 51839.9 | 49909.6 | 49900.6 |  | 52361.2 |  | 51518.8 | 51210.3 | 51201.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59.3 | 57.6 | 57.5 |  | 57.5 |  | 58.5 | 59.1 | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.52 |  | 0.48 | 0.5 | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 |  | 45 | 45 | 44.9 |  | 44.8 |  | 45 | 45.1 | 44.7
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.25 | 0.22 |  | 0.22 |  | 0.22 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.6 | 4.1 | 3.9 |  | 4.1 |  | 4.3 | 4.8 | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 |  | 2.7 | 3.5 | 3.3 |  | 2.9 |  | 3.2 | 3.7 | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 0.7 | 0 | 2.6 | 1 | 0.8 | 0 | 1.4 | 0 | 1.4 | 1.2 | 0.3
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 634.7 |  | 640.4 | 632.8 | 631.87 |  | 640.2 |  | 636.8 | 636.4 | 630.7
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.9 |  | 13.9 | 13.4 | 13.1 |  | 13.4 |  | 13.9 | 13.7 | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 5.3 | 4.5 | 4.1 |  | 4.3 |  | 4.6 | 4.9 | 3.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.3 | 0 | 8.6 | 8.9 | 9 | 0 | 9.1 | 0 | 9.3 | 8.8 | 9.5
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6816.0624 | 0 | 6359.6305 | 6503.3718 | 6566.7783 | 0 | 6727.2748 | 0 | 6838.6143 | 6466.8822 | 6918.7644
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 |  | 0.84 | 0.85 | 0.83 |  | 0.82 |  | 0.81 | 0.85 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.9 |  | 36.4 | 37 | 36.2 |  | 36.3 |  | 35.3 | 36.8 | 36.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 37.3 | 37.7 | 36.9 |  | 36.7 |  | 35.8 | 37.7 | 36.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.7 | 0 | 3.3 | 2.8 | 2.1 | 0 | 2.2 | 0 | 1.6 | 2.9 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.4 |  | 29.3 | 29.5 | 29.3 |  | 29.1 |  | 29 | 29.7 | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.7 |  | 34 | 34.9 | 34.8 |  | 34.5 |  | 34.2 | 34.8 | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 0 | 4.7 | 5.4 | 5.5 | 0 | 5.4 | 0 | 5.2 | 5.1 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1298.8 |  | 1297.1 | 1292.62 | 1295 |  | 1301.4 |  | 1293.9 | 1298.08 | 1298.3
| HEAT CAPACITY | kW | 8226.9 | 0 | 7948.776 | 0 | 7039.6882 | 8060.2171 | 8224.5958 | 0 | 8114.9654 | 0 | 7769.3764 | 7644.582 | 8095.6351
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.47 | 0.46 |  | 0.46 |  | 0.46 | 0.47 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 |  | 19.4 | 20 | 19.8 |  | 19.5 |  | 19.6 | 20.3 | 20.1
| LIQUID LEVEL | mm | mm |  | 200.5 |  | 121.3 | 201.6 | 202.4 |  | 208.8 |  | 170.6 | 198.1 | 204.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 6.09 |  | 5.66 | 5.63 | 5.77 |  | 5.68 |  | 5.87 | 5.27 | 5.37
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 26
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-26
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 74.3 | 70 |  | 81 |  | 73.2 |  | 73.5 |  | 74.6 | 70.3 | 73.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.6 |  | 0 |  | 0 |  | 0.1 |  | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.9 | 64 |  | 77 |  | 69.8 |  | 71.3 |  | 70.2 | 66.9 | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.8 | 70 |  | 70.7 |  | 64.7 |  | 68 |  | 74.6 | 74.8 | 67.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 39 | 37.2 |  | 53 |  | 38.2 |  | 36.5 |  | 54.6 | 35.7 | 35.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6. |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 119.8 | 114.5 |  | 117.3 |  | 114.7 |  | 115.8 |  | 116.3 | 118.1 | 114.8
| INPUT | Kw | 1194kW | 1155 | 1128 |  | 1200 |  | 1181 |  | 1189 |  | 1194 | 1190 | 1172
COMPRESSOR | RUNNING TIME | Hr | NA | 50967.3 | 50958.7 |  | 51849.8 |  | 49920 |  | 52371.3 |  | 51529 | 51234.3 | 51226.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.3. | 58.1 |  | 59.4 |  | 57.8 |  | 57.4 |  | 58.7 | 59.2 | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.58 |  | 0.52 |  | 0.49 | 0.5 | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.2 | 45.1 |  | 44.8 |  | 45 |  | 45 |  | 44.9 | 45.2 | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.82 | 0.23 |  | 0.21 |  | 0.22 |  | 0.22 |  | 0.22 | 0.24 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.9 | 4.2 |  | 3.4 |  | 4.1 |  | 4.1 |  | 4.4 | 5.2 | 3.9
| SATURATION TEMPERATURE | CELCIUS | C | 3.4 | 3.6 |  | 2.4 |  | 3.3 |  | 3 |  | 3.5 | 4.4 | 2.9
| APPROACH TEMP | CELCIUS | C | 1.9 | 1 | 0 | 2.7 | 0 | 0.7 | 0 | 1.3 | 0 | 1.1 | 1.2 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 694.8 | 640.6 |  | 659.1 |  | 642.9 |  | 639.5 |  | 639.7 | 681.9 | 634.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.5 | 14 |  | 13.8 |  | 13.1 |  | 13.6 |  | 13.8 | 13.9 | 12.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5.3 | 4.6 |  | 5.1 |  | 4 |  | 4.3 |  | 4.6 | 5.6 | 3.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.2 | 9.4 | 0 | 8.7 | 0 | 9.1 | 0 | 9.3 | 0 | 9.2 | 8.3 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW | 6578.9376 | 6953.3949 | 0 | 6621.4434 | 0 | 6755.6467 | 0 | 6867.6097 | 0 | 6795.8891 | 6535.5312 | 6519.8152
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.82 |  | 0.83 |  | 0.82 |  | 0.82 |  | 0.82 | 0.83 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.9 | 35.4 |  | 36.1 |  | 35.8 |  | 35.9 |  | 35.2 | 35.8 | 35.3
| SATURATED TEMEPRATURE | CELCIUS | C | 36.4 | 36 |  | 37 |  | 36.5 |  | 36.4 |  | 35.6 | 36.9 | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 1.7 | 0 | 3.1 | 0 | 2.1 | 0 | 2.4 | 0 | 1.5 | 2.5 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.2 | 29 |  | 28.8 |  | 29 |  | 28.9 |  | 28.6 | 28.9 | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.7 | 34.3 |  | 33.9 |  | 34.4 |  | 34 |  | 34.1 | 34.4 | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.3 | 0 | 5.1 | 0 | 5.4 | 0 | 5.1 | 0 | 5.5 | 5.5 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1261.1 | 1295.7 |  | 1294.9 |  | 1299 |  | 1293.4 |  | 1291.9 | 1294 | 1299
| HEAT CAPACITY | kW | 8226.9 | 8009.2956 | 7929.8037 | 0 | 7625.8545 | 0 | 8100 | 0 | 7617.0208 | 0 | 8204.9076 | 8218.2448 | 7800
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.45 |  | 0.46 |  | 0.46 |  | 0.46 |  | 0.45 | 0.48 | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.5 | 19.7 |  | 19.1 |  | 19.5 |  | 19.6 |  | 19.2 | 20.4 | 19.3
| LIQUID LEVEL | mm | mm | 202.5 | 205.8 |  | 127.3 |  | 199.3 |  | 205 |  | 156.8 | 268.9 | 212.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 6 | 6.1 |  | 5.38 |  | 5.69 |  | 5.86 |  | 5.73 | 5.32 | 5.59
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 27
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-27
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.6 |  | 77.4 | 75.2 | 74.3 | 76.3 | 75.7 |  | 74.3 |  | 73.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.9 |  | 72.1 | 70.1 | 68.4 | 71.8 | 72.4 |  | 69.2 |  | 68.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.8 |  | 70.7 | 64.6 | 64.7 | 67.2 | 67.6 |  | 74.6 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.9 |  | 49.4 | 37.1 | 36.1 | 33.6 | 33.4 |  | 53.6 |  | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.1 |  | 116.2 | 117.7 | 117.4 | 118.5 | 118.9 |  | 118.9 |  | 119.3
| INPUT | Kw | 1194kW |  | 1147 |  | 1175 | 1189 | 1176 | 1204 | 1204 |  | 1200 |  | 1202
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50980 |  | 51860 | 49940.1 | 49930 | 52391.7 | 52381.5 |  | 51539 |  | 51250
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 |  | 59.2 | 57.7 | 57.6 | 57.5 | 57.5 |  | 58.7 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 45 | 45.1 | 44.9 | 44.9 | 45 |  | 44.9 |  | 44.7
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.6 | 4.1 | 3.9 | 4.1 | 4.1 |  | 4.4 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 |  | 2.7 | 3.4 | 3.3 | 3 | 3 |  | 3.3 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 0.5 | 0 | 2.2 | 0.7 | 1.3 | 1.4 | 1 | 0 | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 628.88 |  | 631.92 | 636.82 | 638 | 638.3 | 634.64 |  | 637.68 |  | 646.72
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.5 | 13.3 | 13.4 | 13.6 | 13.5 |  | 13.4 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.4 |  | 4.9 | 4.1 | 4.6 | 4.4 | 4 |  | 4.4 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.1 | 0 | 8.6 | 9.2 | 8.8 | 9.2 | 9.5 | 0 | 9 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6608.3233 | 0 | 6275.418 | 6765.2933 | 6483.1409 | 6781.0162 | 6961.9861 | 0 | 6627.1594 | 0 | 6422.3926
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 | 0.84 | 0.84 | 0.83 | 0.84 |  | 0.82 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.2 |  | 36.6 | 36.6 | 36.5 | 36.7 | 36.6 |  | 35.8 |  | 36.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.7 |  | 37.5 | 37.2 | 37.2 | 37.1 | 37.1 |  | 36.3 |  | 37.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.3 | 1 | 3.6 | 2 | 2.8 | 2.2 | 3 | 0 | 2.3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.2 |  | 29 | 29.7 | 29 | 29.6 | 28.9 |  | 29 |  | 29.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.4 |  | 33.9 | 35.2 | 34.4 | 34.9 | 34.1 |  | 34 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 0 | 4.9 | 5.5 | 5.4 | 5.3 | 5.2 | 0 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1301.16 |  | 1300.6 | 1307.7 | 1306.76 | 1296.7 | 1288.98 |  | 1291.22 |  | 1297.94
| HEAT CAPACITY | kW | 8226.9 | 0 | 7812.97 | 0 | 7359.0531 | 8305.254 | 8148.388 | 7935.9238 | 7739.8337 | 0 | 7455.0808 | 0 | 7793.6351
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.46 | 0.47 | 0.47 | 0.46 |  | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 |  | 19.8 | 19.9 | 19.9 | 26 | 19.8 |  | 19.5 |  | 20.3
| LIQUID LEVEL | mm | mm |  | 189.3 |  | 127 | 205.5 | 209.5 | 208.4 | 216 |  | 160.5 |  | 201.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.77 |  | 5.59 | 5.67 | 5.65 | 5.65 | 5.72 |  | 5.63 |  | 5.22
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 28
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-28
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 76.2 | 70.6 |  | 80.8 |  | 75.3 |  | 75.4 | 79 | 74.3 |  | 74
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.4 | 0.6 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 71.6 | 63.9 |  | 76.9 |  | 71 |  | 70.4 | 46.8 | 71 |  | 68.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69 | 69.8 |  | 69.4 |  | 64.6 |  | 68.7 | 76.6 | 74.4 |  | 76.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 40.4 | 37.9 |  | 53.1 |  | 39.4 |  | 34.5 | 58.7 | 45 |  | 45.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 116.3 | 117.1 |  | 117.5 |  | 117.7 |  | 117.1 | 118.3 | 117.4 |  | 117.8
| INPUT | Kw | 1194kW | 1146 | 1147 |  | 1194 |  | 1191 |  | 1192 | 1201 | 1197 |  | 1191
COMPRESSOR | RUNNING TIME | Hr | NA | 50999 | 50990 |  | 51868 |  | 49939 |  | 52398.1 | 51556.9 | 51550.7 |  | 51259
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.3 | 58 |  | 59.2 |  | 57.9 |  | 57.5 | 58.3 | 58.5 |  | 59
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.58 |  | 0.52 | 0.48 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 45.1 |  | 45 |  | 44.9 |  | 44.8 | 45.1 | 45 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.23 |  | 0.21 |  | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.5 | 4.3 |  | 3.3 |  | 4 |  | 4.1 | 3.9 | 4.5 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 2.9 | 3.9 |  | 2 |  | 3.3 |  | 2.8 | 2.8 | 2.8 |  | 3.2
| APPROACH TEMP | CELCIUS | C | 1.4 | 0.5 | 0 | 2.1 | 0 | 1.2 | 0 | 1.1 | 1.3 | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 639.1 | 628.88 |  | 633.04 |  | 629.52 |  | 623.68 | 635.4 | 636.4 |  | 635.76
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.8 | 13.5 |  | 13 |  | 13.5 |  | 13.6 | 13.8 | 13 |  | 12.9
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 4.4 |  | 4.1 |  | 4.5 |  | 3.9 | 4.1 | 3.9 |  | 4.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9.5 | 9.1 | 0 | 8.9 | 0 | 9 | 0 | 9.7 | 9.7 | 9.1 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 7010.9122 | 6608.3233 | 0 | 6505.8383 | 0 | 6542.3557 | 0 | 6985.7921 | 7117.067 | 6687.3441 | 0 | 6386.9654
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.83 |  | 0.81 |  | 0.8 |  | 0.79 | 0.8 | 0.77 |  | 0.8
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.2 | 36.2 |  | 36.2 |  | 35.9 |  | 36 | 33.8 | 35.3 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C | 34.8 | 36.7 |  | 36 |  | 35.6 |  | 35.4 | 34.4 | 34.6 |  | 35.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.6 | 2.3 | 1 | 3.7 | 0 | 2.8 | 0 | 2.9 | 1.6 | 2.4 | 0 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.5 | 29.2 |  | 27.3 |  | 27.4 |  | 27.1 | 27.4 | 27.2 |  | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.2 | 34.4 |  | 32.3 |  | 32.8 |  | 32.5 | 32.8 | 32.2 |  | 32.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.7 | 5.2 | 0 | 5 | 0 | 5.4 | 0 | 5.4 | 5.4 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1295.1 | 1301.16 |  | 1296.4 |  | 1295 |  | 1299.2 | 1297.5 | 1291.36 |  | 1293.6
| HEAT CAPACITY | kW | 8226.9 | 8524.3303 | 7812.97 | 0 | 7484.9885 | 0 | 8075.0577 | 0 | 8101.2471 | 8090.6467 | 7455.8891 | 0 | 7767.5751
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.44 | 0.47 |  | 0.45 |  | 0.46 |  | 0.46 | 0.43 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 18.4 | 20.1 |  | 19.1 |  | 19.2 |  | 19.6 | 17.9 | 19.1 |  | 20
| LIQUID LEVEL | mm | mm | 207.5 | 189.3 |  | 132.2 |  | 207.1 |  | 219.1 | 158.9 | 162.5 |  | 195.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 6.18 | 5.77 |  | 5.57 |  | 5.64 |  | 5.7 | 5.96 | 5.8 |  | 5.57
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 29
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-29
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 76.2 | 70.6 |  | 80.8 |  | 75.3 |  | 75.4 | 79 | 74.3 |  | 74
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.4 | 0.6 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 71.6 | 63.9 |  | 76.9 |  | 71 |  | 70.4 | 46.8 | 71 |  | 68.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69 | 69.8 |  | 69.4 |  | 64.6 |  | 68.7 | 76.6 | 74.4 |  | 76.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 40.4 | 37.9 |  | 53.1 |  | 39.4 |  | 34.5 | 58.7 | 45 |  | 45.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 116.3 | 117.1 |  | 117.5 |  | 117.7 |  | 117.1 | 118.3 | 117.4 |  | 117.8
| INPUT | Kw | 1194kW | 1146 | 1147 |  | 1194 |  | 1191 |  | 1192 | 1201 | 1197 |  | 1191
COMPRESSOR | RUNNING TIME | Hr | NA | 50999 | 50990 |  | 51868 |  | 49939 |  | 52398.1 | 51556.9 | 51550.7 |  | 51259
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.3 | 58 |  | 59.2 |  | 57.9 |  | 57.5 | 58.3 | 58.5 |  | 59
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.58 |  | 0.52 | 0.48 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 45.1 |  | 45 |  | 44.9 |  | 44.8 | 45.1 | 45 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.23 |  | 0.21 |  | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.5 | 4.3 |  | 3.3 |  | 4 |  | 4.1 | 3.9 | 4.5 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 2.9 | 3.9 |  | 2 |  | 3.3 |  | 2.8 | 2.8 | 2.8 |  | 3.2
| APPROACH TEMP | CELCIUS | C | 1.4 | 0.5 | 0 | 2.1 | 0 | 1.2 | 0 | 1.1 | 1.3 | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 639.1 | 628.88 |  | 633.04 |  | 629.52 |  | 623.68 | 635.4 | 636.4 |  | 635.76
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.8 | 13.5 |  | 13 |  | 13.5 |  | 13.6 | 13.8 | 13 |  | 12.9
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 4.4 |  | 4.1 |  | 4.5 |  | 3.9 | 4.1 | 3.9 |  | 4.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9.5 | 9.1 | 0 | 8.9 | 0 | 9 | 0 | 9.7 | 9.7 | 9.1 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 7010.9122 | 6608.3233 | 0 | 6505.8383 | 0 | 6542.3557 | 0 | 6985.7921 | 7117.067 | 6687.3441 | 0 | 6386.9654
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.83 |  | 0.81 |  | 0.8 |  | 0.79 | 0.8 | 0.77 |  | 0.8
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.2 | 36.2 |  | 36.2 |  | 35.9 |  | 36 | 33.8 | 35.3 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C | 34.8 | 36.7 |  | 36 |  | 35.6 |  | 35.4 | 34.4 | 34.6 |  | 35.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.6 | 2.3 | 1 | 3.7 | 0 | 2.8 | 0 | 2.9 | 1.6 | 2.4 | 0 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.5 | 29.2 |  | 27.3 |  | 27.4 |  | 27.1 | 27.4 | 27.2 |  | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.2 | 34.4 |  | 32.3 |  | 32.8 |  | 32.5 | 32.8 | 32.2 |  | 32.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.7 | 5.2 | 0 | 5 | 0 | 5.4 | 0 | 5.4 | 5.4 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1295.1 | 1301.16 |  | 1296.4 |  | 1295 |  | 1299.2 | 1297.5 | 1291.36 |  | 1293.6
| HEAT CAPACITY | kW | 8226.9 | 8524.3303 | 7812.97 | 0 | 7484.9885 | 0 | 8075.0577 | 0 | 8101.2471 | 8090.6467 | 7455.8891 | 0 | 7767.5751
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.44 | 0.47 |  | 0.45 |  | 0.46 |  | 0.46 | 0.43 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 18.4 | 20.1 |  | 19.1 |  | 19.2 |  | 19.6 | 17.9 | 19.1 |  | 20
| LIQUID LEVEL | mm | mm | 207.5 | 189.3 |  | 132.2 |  | 207.1 |  | 219.1 | 158.9 | 162.5 |  | 195.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 6.18 | 5.77 |  | 5.57 |  | 5.64 |  | 5.7 | 5.96 | 5.8 |  | 5.57
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 30
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-06-30
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK |  | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.5 | 70.6 | 82.5 |  | 74.9 |  | 77.2 | 79 | 76.5 |  | 73.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.8 | 0.6 | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.2 | 63.9 | 79.2 |  | 69.2 |  | 72.5 | 46.8 | 71.1 |  | 67.4
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69 | 69.8 | 69.7 |  | 65.2 |  | 69.4 | 76.6 | 73.6 |  | 71.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 39.3 | 37.9 | 55.6 |  | 41.7 |  | 37.1 | 58.7 | 58.3 |  | 64.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.5 | 117.1 | 119.8 |  | 117.4 |  | 118.6 | 118.3 | 119.5 |  | 117.4
| INPUT | Kw | 1194kW |  | 1141 | 1147 | 1211 |  | 1179 |  | 1202 | 1201 | 1194 |  | 1182
COMPRESSOR | RUNNING TIME | Hr | NA |  | 51016.3 | 50990 | 51887.4 |  | 49975.7 |  | 52433.2 | 51556.9 | 51580.9 |  | 51276.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 59.1 | 58 | 59.5 |  | 57.8 |  | 57.6 | 58.3 | 58.3 |  | 60.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.53 | 0.49 |  | 0.59 |  | 0.59 | 0.48 | 0.47 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.7 | 45.1 | 44.9 |  | 44.8 |  | 44.8 | 45.1 | 44.6 |  | 45.6
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.24 | 0.23 | 0.22 |  | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 | 4.3 | 3.3 |  | 3.9 |  | 4 | 3.9 | 4.2 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 | 3.9 | 2.3 |  | 3.3 |  | 3 | 2.8 | 2.9 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0.5 | 2.3 | 0 | 1.1 | 0 | 1 | 1.3 | 1 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 649.76 | 628.88 | 626.08 |  | 634.48 |  | 635.68 | 635.4 | 646.8 |  | 627.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 | 13.5 | 13.7 |  | 13.5 |  | 13.6 | 13.8 | 13 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 | 4.4 | 4.6 |  | 4.4 |  | 4 | 4.1 | 3.9 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.8 | 9.1 | 9.1 | 0 | 9.1 | 0 | 9.6 | 9.7 | 9.1 | 0 | 9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6602.642 | 6608.3233 | 6578.9007 | 0 | 6667.1686 | 0 | 7046.7991 | 7117.067 | 6796.6282 | 0 | 6522.4018
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 | 0.83 | 0.83 |  | 0.82 |  | 0.82 | 0.8 | 0.79 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.3 | 36.2 | 35.9 |  | 35.6 |  | 35.6 | 33.8 | 34.8 |  | 34.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.9 | 36.7 | 36.9 |  | 36.4 |  | 36.3 | 34.4 | 35.4 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.5 | 2.3 | 3.8 | 0 | 2.9 | 0 | 3 | 1.6 | 2.3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.3 | 29.2 | 28.1 |  | 28.1 |  | 27.9 | 27.4 | 28 |  | 28.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.4 | 34.4 | 33.1 |  | 33.5 |  | 33.3 | 32.8 | 33.1 |  | 33.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 5.2 | 5 | 0 | 5.4 | 0 | 5.4 | 5.4 | 5.1 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1300.6 | 1301.16 | 1296.54 |  | 1293.46 |  | 1292.48 | 1297.5 | 1264.76 |  | 1287.72
| HEAT CAPACITY | kW | 8226.9 | 0 | 7659.4226 | 7812.97 | 7485.7968 | 0 | 8065.455 | 0 | 8059.3441 | 8090.6467 | 7448.3557 | 0 | 7732.2679
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.47 | 0.46 |  | 0.46 |  | 0.46 | 0.43 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.5 | 20.1 | 18.8 |  | 19.3 |  | 19.4 | 17.9 | 18.9 |  | 19.7
| LIQUID LEVEL | mm | mm |  | 195 | 189.3 | 119.6 |  | 201.4 |  | 215.7 | 158.9 | 157.6 |  | 226
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.79 | 5.77 | 5.8 |  | 5.76 |  | 5.72 | 5.96 | 5.64 |  | 5.49
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO