## 1
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-01
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 62.8 |  | 78.8 | 72 | 74.9 |  | 77.3 | 80 | 77.1 |  | 72.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 55.5 |  | 74.3 | 68.7 | 70.2 |  | 73.2 | 75.9 | 72.2 |  | 67
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.5 |  | 67.8 | 64.2 | 64.2 |  | 66.2 | 74.8 | 72.2 |  | 72.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 43.3 |  | 58.6 | 40.2 | 41.6 |  | 36.5 | 59.1 | 49.3 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 110.5 |  | 117.6 | 115.9 | 117.3 |  | 119.9 | 117.4 | 118.8 |  | 116.9
| INPUT | Kw | 1194kW |  | 1081 |  | 1176 | 1172 | 1192 |  | 1201 | 1202 | 1191 |  | 1166
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49371.2 |  | 50580.1 | 482190 | 48209.2 |  | 50606.2 | 49794.2 | 49784.4 |  | 49951.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 62.4 |  | 59.3 | 57.6 | 58.2 |  | 57.6 | 58.3 | 58.8 |  | 60.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 | 0.58 | 0.58 |  | 0.52 | 0.47 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 51.7 |  | 45.4 | 45.2 | 44.9 |  | 44.9 | 44.8 | 44.9 |  | 46.6
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.22 | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 |  | 3.2 | 4.1 | 4.3 |  | 3.9 | 3.7 | 3.9 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 |  | 2.4 | 3.3 | 3.6 |  | 2.7 | 2.6 | 2.7 |  | 3.4
| APPROACH TEMP | CELCIUS | C |  | 0.3 | 0 | 1.9 | 0.8 | 0.9 | 0 | 0.9 | 1.4 | 1.2 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 658.32 |  | 641.2 | 653.8 | 640.56 |  | 621.36 | 663 | 638.84 |  | 634.32
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.8 |  | 12.8 | 13.2 | 13.4 |  | 13.2 | 13.4 | 12.8 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.3 |  | 4.3 | 4.1 | 4.5 |  | 3.6 | 4 | 3.9 |  | 4.4
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8.5 | 0 | 8.5 | 9.1 | 8.9 | 0 | 9.6 | 9.4 | 8.9 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW |  | 6461.5704 | 0 | 6293.5335 | 6870.1848 | 6583.1224 | 0 | 6888.0554 | 7196.5358 | 6565.4457 | 0 | 6445.746
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 |  | 0.83 | 0.79 | 0.82 |  | 0.82 | 0.76 | 0.73 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 34.6 |  | 35.7 | 34.8 | 35.6 |  | 35.6 | 33.6 | 34.9 |  | 35.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.1 |  | 36.9 | 35.5 | 36.6 |  | 36.4 | 34.3 | 35.4 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  |  | 2.5 | 0 | 3.7 | 2.3 | 2.8 | 0 | 3.1 | 1.6 | 2 | 0 | 3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.9 |  | 27.7 | 27.7 | 27.8 |  | 27.6 | 27.2 | 27.7 |  | 27.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.6 |  | 33.2 | 33.2 | 33.8 |  | 33.3 | 32.7 | 33.4 |  | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.7 | 0 | 5.5 | 5.5 | 6 | 0 | 5.7 | 5.5 | 5.7 | 0 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1145.2 |  | 1156.4 | 1298.9 | 1184.68 |  | 1154.86 | 1299.9 | 1128.26 |  | 1178.52
| HEAT CAPACITY | kW | 8226.9 |  | 7537.6905 | 0 | 7344.3418 | 8249.3649 | 8207.9446 | 0 | 7601.2725 | 8255.7159 | 7426.1917 | 0 | 7757.0023
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 | 0.45 | 0.45 |  | 0.45 | 0.43 | 0.44 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.9 |  | 18.8 | 18.7 | 18.9 |  | 19.3 | 17.6 | 18.6 |  | 19.7
| LIQUID LEVEL | mm | mm |  | 165 |  | 119.2 | 209.1 | 196.3 |  | 198.7 | 159.5 | 160.9 |  | 209.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.46 |  | 5.57 | 5.72 | 5.55 |  | 5.48 | 5.78 | 5.53 |  | 5.5
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 2
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-02
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 69.1 |  | 81.6 |  | 73.8 |  | 70 |  | 75.8 |  | 72.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.4 |  | 0 |  | 0 |  | 0 |  | 0.2 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 62.6 |  | 77.9 |  | 67.8 |  | 65.2 |  | 71.6 |  | 67.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.7 |  | 66.9 |  | 63.6 |  | 66.2 |  | 73.3 |  | 70.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.9 |  | 52 |  | 39.3 |  | 34.9 |  | 53.8 |  | 43.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.5 |  | 118.3 |  | 116 |  | 111.7 |  | 116.6 |  | 115.5
| INPUT | Kw | 1194kW |  | 1131 |  | 1189 |  | 1178 |  | 1135 |  | 1191 |  | 1171
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49381 |  | 50590.3 |  | 48227.2 |  | 50616.3 |  | 49806.2 |  | 49961.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 |  | 59.1 |  | 57.8 |  | 57.2 |  | 58.6 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.48 |  | 0.59 |  | 0.59 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.3 |  | 44.9 |  | 44.8 |  | 45.3 |  | 44.6 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 |  | 0.23 |  | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 |  | 2.9 |  | 4.6 |  | 3.6 |  | 4 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2 |  | 3.4 |  | 2.9 |  | 3 |  | 3.4
| APPROACH TEMP | CELCIUS | C |  | 0.6 | 0 | 2 | 0 | 1.2 | 0 | 1 | 0 | 1 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 655.04 |  | 640.56 |  | 639.04 |  | 630.4 |  | 638.64 |  | 637.84
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.9 |  | 12.7 |  | 13.5 |  | 13.2 |  | 13 |  | 12.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.4 |  | 4 |  | 4.6 |  | 3.9 |  | 4 |  | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8.5 | 0 | 8.7 | 0 | 8.9 | 0 | 9.3 | 0 | 9 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW |  | 6429.3764 | 0 | 6435.1871 | 0 | 6567.5012 | 0 | 6769.8845 | 0 | 6637.1363 | 0 | 6260.5543
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.83 |  | 0.82 |  | 0.82 |  | 0.8 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.7 |  | 35.9 |  | 35.6 |  | 35.4 |  | 35 |  | 35.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 36.9 |  | 36.4 |  | 36.3 |  | 35.5 |  | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  |  | 2.5 | 0 | 3.9 | 0 | 3 | 0 | 3.1 | 0 | 2.3 | 0 | 3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.7 |  | 27.5 |  | 27.6 |  | 27.4 |  | 27.5 |  | 27.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.9 |  | 33 |  | 33.4 |  | 33.2 |  | 33.2 |  | 33.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 6.2 | 0 | 5.5 | 0 | 5.8 | 0 | 5.8 | 0 | 5.7 | 0 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1044.4 |  | 1172.22 |  | 1198.54 |  | 1170.12 |  | 1143.24 |  | 1195.88
| HEAT CAPACITY | kW | 8226.9 |  | 7477.2286 | 0 | 7444.8152 | 0 | 8027.1732 | 0 | 7836.8314 | 0 | 7524.7898 | 0 | 7595.0808
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 |  | 0.46 |  | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 |  | 18.7 |  | 19.2 |  | 19.4 |  | 19.3 |  | 19.5
| LIQUID LEVEL | mm | mm |  | 200 |  | 129.8 |  | 208.2 |  | 200.1 |  | 157.1 |  | 203.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.66 |  | 5.37 |  | 5.65 |  | 5.8 |  | 5.74 |  | 5.42
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 3
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-03
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 62.8 |  | 78.8 | 76.3 | 74.9 | 76.7 | 77.3 |  | 77.1 |  | 72.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 | 0 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 55.5 |  | 74.3 | 70.7 | 70.2 | 72.7 | 73.2 |  | 72.2 |  | 67
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.5 |  | 67.8 | 63.9 | 64.2 | 67.1 | 66.2 |  | 72.2 |  | 72.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 43.3 |  | 58.6 | 43.9 | 41.6 | 38.2 | 36.5 |  | 49.3 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 110.5 |  | 117.6 | 116.4 | 117.3 | 117.2 | 119.9 |  | 118.8 |  | 116.9
| INPUT | Kw | 1194kW |  | 1081 |  | 1176 | 1178 | 1192 | 1194 | 1201 |  | 1191 |  | 1166
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49390.5 |  | 50615 | 48245.7 | 48237 | 50635 | 50626.3 |  | 49816.2 |  | 49979.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 |  | 59.3 | 57.2 | 58.2 | 57.1 | 57.6 |  | 58.8 |  | 60.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 | 0.58 | 0.58 | 0.52 | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 51.7 |  | 45.4 | 44.6 | 44.9 | 44.9 | 44.9 |  | 44.9 |  | 46.6
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.22 | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 |  | 3.2 | 3.7 | 4.3 | 3.8 | 3.9 |  | 3.9 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 |  | 2.4 | 2.9 | 3.6 | 2.8 | 2.7 |  | 2.7 |  | 3.4
| APPROACH TEMP | CELCIUS | C |  | 0.2 | 0 | 1.7 | 1.3 | 0.8 | 1.5 | 1.1 | 0 | 1.2 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 651.2 |  | 642.08 | 646.9 | 641.04 | 657.2 | 622.4 |  | 638.48 |  | 639.68
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.9 |  | 12.7 | 13.3 | 13.4 | 13.5 | 13.1 |  | 13.1 |  | 13
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.2 |  | 4.1 | 4.2 | 4.4 | 4.3 | 3.8 |  | 3.9 |  | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8.7 | 0 | 8.6 | 9.1 | 9 | 9.2 | 9.3 | 0 | 9.2 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW |  | 6542.0785 | 0 | 6376.3141 | 6797.679 | 6662.0785 | 6981.8014 | 6683.9723 | 0 | 6782.9284 | 0 | 6426.3464
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 |  | 0.82 | 0.79 | 0.81 | 0.79 | 0.81 |  | 0.79 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 34.6 |  | 35.7 | 35.7 | 35.6 | 34.5 | 35.6 |  | 34.9 |  | 35.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.7 |  | 36.5 | 35.4 | 36.2 | 35.3 | 35.9 |  | 35.3 |  | 35.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  |  | 2.6 | 0 | 3.7 | 2.2 | 2.9 | 2.5 | 3 | 0 | 2.3 | 0 | 2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.4 |  | 27.2 | 27.6 | 27.4 | 27.5 | 27.1 |  | 27.2 |  | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.1 |  | 32.8 | 33.2 | 33.3 | 32.8 | 32.9 |  | 33 |  | 33.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.7 | 0 | 5.6 | 5.6 | 5.9 | 5.3 | 5.8 | 0 | 5.8 | 0 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1161.3 |  | 1155.98 | 1302.4 | 1179.36 | 1290.1 | 1155.42 |  | 1130.08 |  | 1175.44
| HEAT CAPACITY | kW | 8226.9 |  | 7643.6605 | 0 | 7475.1594 | 8421.9861 | 8034.9007 | 7895.5312 | 7738.3788 | 0 | 7568.6651 | 0 | 7872.4619
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 | 0.44 | 0.45 | 0.45 | 0.45 |  | 0.44 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.9 |  | 18.8 | 18.2 | 18.9 | 18.8 | 19.3 |  | 18.6 |  | 19.7
| LIQUID LEVEL | mm | mm |  | 165 |  | 119.2 | 215.1 | 196.3 | 213.5 | 198.7 |  | 160.9 |  | 209.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.46 |  | 5.57 | 5.72 | 5.55 | 5.57 | 5.48 |  | 5.53 |  | 5.5
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 4
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-04
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 74 | 70.6 |  | 80 |  | 74 |  | 71.4 | 80 | 75.6 |  | 73.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.1 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 69 | 64.7 |  | 76.2 |  | 69 |  | 67.8 | 76.1 | 71 |  | 67.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.6 | 67.4 |  | 68.8 |  | 63.6 |  | 66.3 | 75.3 | 73.4 |  | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 37.4 | 36.2 |  | 50.9 |  | 39.9 |  | 33.9 | 53 | 52.3 |  | 42.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 117.4 | 117.2 |  | 118.1 |  | 116.7 |  | 113.9 | 118.5 | 118.6 |  | 186.2
| INPUT | Kw | 1194kW | 1158 | 1147 |  | 1194 |  | 1181 |  | 1161 | 1217 | 1208 |  | 1182
COMPRESSOR | RUNNING TIME | Hr | NA | 49407.8 | 49398.5 |  | 50623.9 |  | 48255.4 |  | 50648.2 | 49834.4 | 49825.1 |  | 49988.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 58.5 |  | 59.4 |  | 57.5 |  | 57.4 | 58.1 | 58.7 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 | 0.48 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.2 | 44.8 |  | 44.8 |  | 45 |  | 44.9 | 45.9 | 44.8 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.8 | 4.3 |  | 3.3 |  | 4.2 |  | 3.9 | 3.9 | 4.6 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C | 3.3 | 4 |  | 2.5 |  | 3.5 |  | 2.8 | 2.9 | 3.6 |  | 3.5
| APPROACH TEMP | CELCIUS | C | 1 | 1 | 0 | 2.5 | 0 | 0.7 | 0 | 1.2 | 1 | 1.2 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 646.4 | 677.3 |  | 649.4 |  | 648.6 |  | 628.6 | 636.88 | 654.8 |  | 642.2
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.2 | 13.5 |  | 13.6 |  | 13.2 |  | 13 | 13.3 | 13.7 |  | 13
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 5 |  | 5 |  | 4.2 |  | 4 | 3.9 | 4.8 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.9 | 8.5 | 0 | 8.6 | 0 | 9 | 0 | 9 | 9.4 | 8.9 | 0 | 8.3
| CHILLING CAPACITY | kW | 7032.6kW | 6643.1409 | 6647.8637 | 0 | 6449.0069 | 0 | 6740.6467 | 0 | 6532.7945 | 6913.0162 | 6729.4688 | 0 | 6155.0346
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.82 |  | 0.85 |  | 0.83 |  | 0.82 | 0.79 | 0.81 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35 | 36.1 |  | 36.6 |  | 36.4 |  | 36.4 | 34.5 | 35.9 |  | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C | 35.8 | 36.7 |  | 37.6 |  | 37.1 |  | 36.7 | 35.3 | 36.3 |  | 37.1
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.7 | 1.8 | 0 | 3.3 | 0 | 2.3 | 0 | 2.2 | 2.5 | 1.5 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.8 | 28.7 |  | 28.7 |  | 28.9 |  | 28.8 | 27.5 | 28.6 |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.1 | 34.9 |  | 34.3 |  | 34.8 |  | 34.5 | 32.8 | 34.8 |  | 34.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.3 | 6.2 | 0 | 5.6 | 0 | 5.9 | 0 | 5.7 | 5.3 | 6.2 | 0 | 5.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1294.44 | 1160.3 |  | 1154.5 |  | 1138.9 |  | 1151.5 | 1282.96 | 1129.4 |  | 1174.1
| HEAT CAPACITY | kW | 8226.9 | 7922.0924 | 8306.9977 | 0 | 7465.5889 | 0 | 7759.2494 | 0 | 7579.157 | 7851.8337 | 8085.7737 | 0 | 7999.0647
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.47 |  | 0.46 |  | 0.46 |  | 0.46 | 0.44 | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.7 | 20.2 |  | 19.5 |  | 19.7 |  | 19.7 | 18.4 | 19.4 |  | 20.1
| LIQUID LEVEL | mm | mm | 208.1 | 201 |  | 122.6 |  | 202.2 |  | 208 | 159.4 | 167.4 |  | 186.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 6.05 | 5.62 |  | 5.36 |  | 5.66 |  | 5.65 | 5.76 | 5.45 |  | 5.23
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 5
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-05
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 67.6 |  | 76 | 76.9 | 73.8 |  | 70 |  | 75.8 | 75.2 | 72.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 |  | 0 |  | 0.2 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 60.9 |  | 71.2 | 71.6 | 67.8 |  | 65.2 |  | 71.6 | 70.2 | 67.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 68.6 |  | 70.7 | 63.8 | 63.6 |  | 66.2 |  | 73.3 | 72.9 | 70.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 34.2 |  | 50.9 | 37.4 | 39.3 |  | 34.9 |  | 53.8 | 41.7 | 43.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 115 |  | 115.9 | 117.8 | 116 |  | 111.7 |  | 116.6 | 118.9 | 115.5
| INPUT | Kw | 1194kW |  | 1143 |  | 1186 | 1194 | 1178 |  | 1135 |  | 1191 | 1212 | 1171
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49416.8 |  | 50634 | 48274.4 | 48265.8 |  | 50658.7 |  | 49847.6 | 50007.2 | 49998.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 |  | 59.8 | 57.6 | 57.8 |  | 57.2 |  | 58.6 | 59.1 | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.59 |  | 0.48 | 0.5 | 0.49
| OIL LEVEL | [5 empty] | m
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 |  | 44.9 | 45.1 | 44.8 |  | 45.3 |  | 44.6 | 45.1 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.23 | 0.23 |  | 0.22 |  | 0.22 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 |  | 2.9 | 3.9 | 4.6 |  | 3.6 |  | 4 | 4.8 | 4.2
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2 | 3.2 | 3.4 |  | 2.9 |  | 3 | 3.9 | 3.4
| APPROACH TEMP | CELCIUS | C |  | 0.6 | 0 | 2 | 1.2 | 1.2 | 0 | 1 | 0 | 1 | 0.8 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 644.4 |  | 645.8 | 634.64 | 641.5 |  | 635.5 |  | 634.1 | 637.36 | 649
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.9 |  | 12.7 | 13.5 | 13.5 |  | 13.2 |  | 13 | 13.5 | 12.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.4 |  | 4 | 4.4 | 4.6 |  | 3.9 |  | 4 | 4.7 | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8.5 | 0 | 8.7 | 9.1 | 8.9 | 0 | 9.3 | 0 | 9 | 8.8 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW |  | 6324.9423 | 0 | 6487.8291 | 6668.8499 | 6592.7829 | 0 | 6824.6536 | 0 | 6589.9538 | 6476.6374 | 6370.0924
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.83 | 0.84 | 0.82 |  | 0.82 |  | 0.8 | 0.84 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.7 |  | 35.9 | 36.3 | 35.6 |  | 35.4 |  | 35 | 36.3 | 35.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 36.9 | 37.1 | 36.4 |  | 36.3 |  | 35.5 | 37.1 | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  |  | 2.5 | 0 | 3.9 | 3.1 | 3 | 0 | 3.1 | 0 | 2.3 | 3.1 | 3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.7 |  | 27.5 | 28.7 | 27.6 |  | 27.4 |  | 27.5 | 28.7 | 27.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.9 |  | 33 | 34 | 33.4 |  | 33.2 |  | 33.2 | 34 | 33.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 6.2 | 0 | 5.5 | 5.3 | 5.8 | 0 | 5.8 | 0 | 5.7 | 5.3 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1160 |  | 1156.9 | 1295.98 | 1184.1 |  | 1153.7 |  | 1135.9 | 1291.36 | 1179.3
| HEAT CAPACITY | kW | 8226.9 |  | 8304.8499 | 0 | 7347.5173 | 7931.5173 | 7930.4619 | 0 | 7726.8591 | 0 | 7476.4781 | 7903.2425 | 7489.7806
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.46 | 0.46 |  | 0.46 |  | 0.45 | 0.47 | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 |  | 18.7 | 19.5 | 19.2 |  | 19.4 |  | 19.3 | 20.2 | 19.5
| LIQUID LEVEL | mm | mm |  | 200 |  | 129.8 | 205.1 | 208.2 |  | 200.1 |  | 157.1 | 201.2 | 203.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.66 |  | 5.37 | 5.63 | 5.65 |  | 5.8 |  | 5.74 | 5.27 | 5.42
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 6
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-06
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 65.5 | 77 | 79 |  | 73.8 | 71.8 | 71.4 |  | 76.1 |  | 72.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 | 0 | 0 |  | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 60.9 | 74.4 | 74.6 |  | 70.7 | 68.8 | 68.7 |  | 70.5 |  | 66.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 68.6 | 71.2 | 70.1 |  | 63.7 | 66.4 | 65.4 |  | 74.1 |  | 73.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 35.9 | 56.8 | 53.8 |  | 38.2 | 32.1 | 33.7 |  | 51.4 |  | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.1 | 115.8 | 118.8 |  | 118.1 | 113.4 | 115.5 |  | 120.3 |  | 118.3
| INPUT | Kw | 1194kW |  | 1131 | 1169 | 1198 |  | 1193 | 1150 | 1170 |  | 1214 |  | 1193
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49426 | 50651.8 | 50643.5 |  | 48289.8 | 50676.6 | 50668.3 |  | 49857.1 |  | 50019.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 | 59.1 | 59.3 |  | 58 | 57.3 | 57.2 |  | 58.9 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.49 | 0.49 |  | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.5
| OIL LEVEL | [5 empty] | m
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 | 44.8 | 44.8 |  | 45.1 | 45 | 45.1 |  | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.22 | 0.22 |  | 0.22 | 0.22 | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.5 | 3.3 | 3.5 |  | 4.1 | 3.6 | 3.7 |  | 4.6 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.1 | 2.5 | 2.7 |  | 3.3 | 2.8 | 2.7 |  | 3.7 |  | 3.8
| APPROACH TEMP | CELCIUS | C |  | 0.9 | 2.1 | 2.4 | 0 | 0.7 | 1.5 | 1.1 | 0 | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 670.8 | 677.2 | 651.4 |  | 648.9 | 709.6 | 634.6 |  | 656.2 |  | 633.2
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.9 | 12.6 | 13.7 |  | 13 | 12.8 | 12.9 |  | 13.8 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 | 4.6 | 5.1 |  | 4 | 4.3 | 3.8 |  | 4.8 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8.9 | 8 | 8.6 | 0 | 9 | 8.5 | 9.1 | 0 | 9 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW |  | 6893.903 | 6255.8891 | 6468.8684 | 0 | 6743.7644 | 6964.8961 | 6668.4296 | 0 | 6819.6305 | 0 | 6434.3649
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 | 0.82 | 0.84 |  | 0.83 | 0.8 | 0.82 |  | 0.81 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.8 | 35.8 | 36.5 |  | 36.2 | 35.3 | 36.1 |  | 35.6 |  | 36.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 | 36.7 | 37.4 |  | 36.9 | 35.8 | 36.5 |  | 36 |  | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 |  | 2 | 3.6 | 3.3 | 0 | 2.3 | 2.4 | 2.4 | 0 | 1.5 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.6 | 28.2 | 28.4 |  | 28.6 | 28.2 | 28.5 |  | 28.3 |  | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.4 | 33.1 | 34.1 |  | 34.6 | 33.4 | 34.1 |  | 34.5 |  | 34.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.8 | 4.9 | 5.7 | 0 | 6 | 5.2 | 5.6 | 0 | 6.2 | 0 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1160.2 | 1305.9 | 1160.4 |  | 1184.9 | 1295.7 | 1156.8 |  | 1134.8 |  | 1175.6
| HEAT CAPACITY | kW | 8226.9 |  | 7770.3926 | 7389.0416 | 7637.7367 | 0 | 8209.4688 | 7780.1848 | 7480.4619 | 0 | 8124.4342 | 0 | 7873.5335
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.45 | 0.46 |  | 0.45 | 0.45 | 0.46 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 | 18.8 | 19.5 |  | 19.3 | 19 | 19.4 |  | 19.3 |  | 20.2
| LIQUID LEVEL | mm | mm |  | 210.2 | 118.1 | 119.2 |  | 201.1 | 213 | 208.2 |  | 163.9 |  | 200.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.79 | 5.51 | 5.55 |  | 5.51 | 5.68 | 5.58 |  | 5.49 |  | 5.39
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 7
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-07
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 74.5 | 70 |  | 78.6 |  | 75.1 |  | 77.3 | 79.4 | 77.1 |  | 72.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.2 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 69.7 | 64.3 |  | 74.3 |  | 70.2 |  | 73.2 | 75.5 | 72.2 |  | 67
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 68.9 | 66.7 |  | 67.8 |  | 64.2 |  | 66.2 | 75 | 72.2 |  | 72.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 43 | 41.9 |  | 58.6 |  | 41.6 |  | 36.5 | 48 | 49.3 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118 | 117.2 |  | 117.6 |  | 117.3 |  | 119.9 | 119.3 | 118.8 |  | 116.9
| INPUT | Kw | 1194kW | 1159 | 1158 |  | 1189 |  | 1199 |  | 1201 | 1215 | 1191 |  | 1166
COMPRESSOR | RUNNING TIME | Hr | NA | 49443.9 | 49435.2 |  | 50660.2 |  | 48298.9 |  | 50688.1 | 49875.3 | 49866.3 |  | 50028.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 62.4 |  | 59.3 |  | 58.2 |  | 57.6 | 58.4 | 58.8 |  | 60.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  | 0.58 |  | 0.52 | 0.48 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 45.1 |  | 45 |  | 45 |  | 45.2 | 44.9 | 45 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.7 | 4.4 |  | 3.7 |  | 4.6 |  | 3.8 | 4.1 | 4.5 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 3.4 | 3.9 |  | 2.9 |  | 3.6 |  | 2.9 | 3.5 | 3.7 |  | 3.5
| APPROACH TEMP | CELCIUS | C | 1 | 0.9 | 0 | 1.8 | 0 | 0.7 | 0 | 1.2 | 1 | 0.9 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 651.9 | 659.5 |  | 642 |  | 642.3 |  | 638.2 | 640.4 | 646.4 |  | 638
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.5 | 13.3 |  | 13.6 |  | 13.2 |  | 12.9 | 13.8 | 13.4 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.4 | 4.8 |  | 4.7 |  | 4.3 |  | 4.1 | 4.2 | 4.6 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.9 | 8.5 | 0 | 8.9 | 0 | 8.9 | 0 | 8.8 | 9.4 | 8.8 | 0 | 9
| CHILLING CAPACITY | kW | 7032.6kW | 6643.1409 | 6473.1524 | 0 | 6597.9215 | 0 | 6601.0046 | 0 | 6485.1732 | 6913.0162 | 6568.4988 | 0 | 6630.485
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.79 | 0.82 |  | 0.85 |  | 0.85 |  | 0.83 | 0.79 | 0.82 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.6 | 35.9 |  | 36.6 |  | 36.5 |  | 36.7 | 34.5 | 36.7 |  | 35.3
| SATURATED TEMEPRATURE | CELCIUS | C | 35.2 | 36.5 |  | 37.5 |  | 37.2 |  | 37.2 | 35.3 | 37 |  | 36
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.7 | 2.4 | 0 | 4.2 | 0 | 4 | 0 | 3.3 | 2.5 | 2.1 | 0 | 2.7
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.5 | 27.7 |  | 27.9 |  | 28 |  | 27.8 | 27.5 | 27.7 |  | 27.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.2 | 34.1 |  | 33.3 |  | 33.2 |  | 33.9 | 32.8 | 34.9 |  | 33.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.3 | 6.4 | 0 | 5.4 | 0 | 5.2 | 0 | 6.1 | 5.3 | 7.2 | 0 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1287.8 | 1163.1 |  | 1156.8 |  | 1180.8 |  | 1153.4 | 1269.2 | 1129.9 |  | 1178.6
| HEAT CAPACITY | kW | 8226.9 | 7922.0924 | 8595.6582 | 0 | 7213.3025 | 0 | 7090.254 | 0 | 8124.4111 | 7851.8337 | 9394.0878 | 0 | 7485.3349
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.47 |  | 0.46 |  | 0.47 |  | 0.47 | 0.44 | 0.48 |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C | 18.9 | 20 |  | 19.8 |  | 19.9 |  | 19.9 | 18.4 | 19.8 |  | 19.2
| LIQUID LEVEL | mm | mm | 196.4 | 171.9 |  | 122.3 |  | 206.9 |  | 204.9 | 159.4 | 152.9 |  | 195.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.87 | 5.59 |  | 5.55 |  | 5.5 |  | 5.62 | 5.8 | 5.35 |  | 5.57
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 8
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-08
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  |  |  |  | 76.1 | [5 empty] | 77
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  |  |  |  | 0 | [5 empty] | 0
OPENING OF 2nd VANE |  | % | 0~100% |  |  |  |  | 70.4 | [5 empty] | 72.4
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  |  |  |  | 63.7 | [5 empty] | 72.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  |  |  |  | 36.8 | [5 empty] | 43.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  |  |  |  | 6.6 | [5 empty] | 6.6
| CURRENT | A | ≤115A |  |  |  |  | 117.4 | [5 empty] | 122.1
| INPUT | Kw | 1194kW |  |  |  |  | 1199 | [5 empty] | 1240
COMPRESSOR | RUNNING TIME | Hr | NA |  |  |  |  | 48318 | [5 empty] | 50048.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  |  |  |  | 57.5 | [5 empty] | 59
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  |  |  |  | 0.59 | [5 empty] | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  |  |  |  | 45.1 | [5 empty] | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  |  |  |  | 0.23 | [5 empty] | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  |  |  |  | 4.2 | [5 empty] | 5
| SATURATION TEMPERATURE | CELCIUS | C |  |  |  |  | 3.3 | [5 empty] | 4
| APPROACH TEMP | CELCIUS | C | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  |  |  |  | 637.3 | [5 empty] | 674.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  |  |  |  | 13.1 | [5 empty] | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  |  |  |  | 4.1 | [5 empty] | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 8.4 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 0 | 0 | 0 | 6623.2102 | 0 | 0 | 0 | 0 | 0 | 6546.3741 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  |  |  |  | 0.85 | [5 empty] | 0.85
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  |  |  |  | 36.8 | [5 empty] | 37.1
| SATURATED TEMEPRATURE | CELCIUS | C |  |  |  |  | 37.5 | [5 empty] | 37.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  |  |  |  | 29.8 | [5 empty] | 29.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  |  |  |  | 35.2 | [5 empty] | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 0 | 0 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  |  |  |  | 1292.5 | [5 empty] | 1289
| HEAT CAPACITY | kW | 8226.9 | 0 | 0 | 0 | 0 | 8059.4688 | 0 | 0 | 0 | 0 | 0 | 8037.6443 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  |  |  |  | 0.46 | [5 empty] | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  |  |  |  | 19.9 | [5 empty] | 20.5
| LIQUID LEVEL | mm | mm |  |  |  |  | 203.2 | [5 empty] | 2000.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  |  |  |  | 5.57 | [5 empty] | 5.05
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 9
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-09
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK |  | OK | OK | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 70.6 | 72.2 | 78.8 |  | 75.7 | 76.7 | 77.4 |  | 77.2 |  | 73.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.2 | 0 | 0 |  | 0 | 0 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.3 | 68.6 | 74.3 |  | 70.2 | 72.7 | 73.2 |  | 72.2 |  | 67
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.7 | 66.5 | 67.8 |  | 64.2 | 67.1 | 66.2 |  | 72.2 |  | 72.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 41.9 | 55.1 | 58.6 |  | 41.6 | 38.2 | 36.5 |  | 49.3 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.2 | 112.1 | 117.6 |  | 117.3 | 117.2 | 119.9 |  | 118.8 |  | 116.9
| INPUT | Kw | 1194kW |  | 1159 | 1129 | 1191 |  | 1200 | 1194 | 1199 |  | 1193 |  | 1168
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49462.3 | 50689.5 | 50680.3 |  | 48332.8 | 50717 | 50707.9 |  | 49896.9 |  | 50058
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 62.4 | 58.8 | 59.3 |  | 58.2 | 57.1 | 57.6 |  | 58.8 |  | 60.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.49 |  | 0.58 | 0.52 | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 | 45 | 45 |  | 45 | 44.9 | 45.2 |  | 45 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.22 |  | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 | 2.7 | 3.6 |  | 4.7 | 3.8 | 3.9 |  | 4.5 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 | 1.9 | 2.8 |  | 3.7 | 2.8 | 3 |  | 3.7 |  | 3.6
| APPROACH TEMP | CELCIUS | C |  | 0.9 | 2.7 | 1.8 | 0 | 0.7 | 1.5 | 1.2 |  | 0.9 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 660.1 | 675.12 | 645.2 |  | 644.2 | 657.2 | 639 |  | 647.9 |  | 640.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.3 | 12.9 | 13.6 |  | 13.2 | 13.5 | 12.9 |  | 13.4 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 | 4.6 | 4.6 |  | 4.4 | 4.3 | 4.2 |  | 4.6 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8.6 | 8.3 | 9 | 0 | 8.8 | 9.2 | 8.7 |  | 8.8 | 0 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW |  | 6555.2656 | 6470.5497 | 6705.3118 | 0 | 6546.1432 | 6981.8014 | 6419.515 |  | 6583.7413 | 0 | 6581.4781
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.83 | 0.85 |  | 0.85 | 0.79 | 0.83 |  | 0.82 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 | 35.6 | 36.6 |  | 36.4 | 34.5 | 36.6 |  | 36.2 |  | 35.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.6 | 36.6 | 37.5 |  | 37.1 | 35.3 | 37.1 |  | 36.5 |  | 36
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 |  | 2.4 | 3.7 | 4.2 | 0 | 4 | 2.5 | 3.3 |  | 2 | 0 | 2.7
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.7 | 27.9 | 27.9 |  | 28 | 27.5 | 27.8 |  | 27.7 |  | 27.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.2 | 32.9 | 33.3 |  | 33.1 | 32.8 | 33.8 |  | 34.5 |  | 33.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 6.5 | 5 | 5.4 | 0 | 5.1 | 5.3 | 6 |  | 6.8 | 0 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1164.5 | 1308.86 | 1157.3 |  | 1179.6 | 1290.1 | 1154.5 |  | 1131.9 |  | 1179.2
| HEAT CAPACITY | kW | 8226.9 |  | 8740.4734 | 7556.9284 | 7216.4203 | 0 | 6946.836 | 7895.5312 | 7998.8453 |  | 8887.8984 | 0 | 7489.1455
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.44 | 0.46 |  | 0.47 | 0.45 | 0.47 |  | 0.48 |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 | 18.4 | 19.8 |  | 19.9 | 18.8 | 19.9 |  | 19.8 |  | 19.2
| LIQUID LEVEL | mm | mm |  | 174.3 | 128.7 | 123.3 |  | 206.8 | 213.5 | 205.3 |  | 155.6 |  | 197.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.59 | 5.45 | 5.55 |  | 5.5 | 5.57 | 5.62 |  | 5.35 |  | 5.57
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 10
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-10
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.3 |  | 80.5 |  | 75.5 |  | 73.5 |  | 76.7 |  | 74.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.8 |  | 76.9 |  | 69.8 |  | 68.5 |  | 71.9 |  | 69.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.9 |  | 69.9 |  | 64.8 |  | 66.2 |  | 74.4 |  | 73.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.4 |  | 52.6 |  | 41.1 |  | 34.9 |  | 65.3 |  | 45.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.2 |  | 117.2 |  | 115.8 |  | 114.2 |  | 112.5 |  | 117.3
| INPUT | Kw | 1194kW |  | 1137 |  | 1192 |  | 1180 |  | 1161 |  | 1200 |  | 1193
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49471.2 |  | 50698.6 |  | 48342.3 |  | 50731.6 |  | 49906.6 |  | 50067.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.3 |  | 57.7 |  | 57.2 |  | 58.6 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.48 |  | 0.59 |  | 0.44 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.7 |  | 44.7 |  | 44.9 |  | 44.8 |  | 44.9 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.1 |  | 3.3 |  | 4.1 |  | 3.6 |  | 4.4 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.3 |  | 3.2 |  | 2.7 |  | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C |  | 0.8 | 0 | 2.3 | 0 | 1.2 | 0 | 1 |  | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 663.84 |  | 643.44 |  | 638.4 |  | 636 |  | 649.04 |  | 635.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.2 |  | 13.4 |  | 13.5 |  | 12.9 |  | 13.4 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.6 |  | 4.4 |  | 3.7 |  | 4.4 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8.6 | 0 | 8.8 | 0 | 9.1 | 0 | 9.2 |  | 9 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW |  | 6592.4065 | 0 | 6538.4203 | 0 | 6708.3603 | 0 | 6756.582 |  | 6745.2194 | 0 | 6458.7529
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 |  | 0.83 |  | 0.82 |  | 0.81 |  | 0.79 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.3 |  | 36 |  | 35.6 |  | 35.5 |  | 34.9 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36 |  | 36.9 |  | 36.4 |  | 35.9 |  | 35.4 |  | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 |  | 2.7 | 0 | 4 | 0 | 3.1 | 0 | 3.1 |  | 2.3 | 0 | 3.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.5 |  | 27.2 |  | 27.4 |  | 27.1 |  | 27.2 |  | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.3 |  | 32.9 |  | 33.3 |  | 32.8 |  | 33.1 |  | 33.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.8 | 0 | 5.7 | 0 | 5.9 | 0 | 5.7 |  | 5.9 | 0 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1155.98 |  | 1149.68 |  | 1176.56 |  | 1150.66 |  | 1129.8 |  | 1170.4
| HEAT CAPACITY | kW | 8226.9 |  | 7742.1293 | 0 | 7567.1778 | 0 | 8015.8245 | 0 | 7573.6282 |  | 7697.2517 | 0 | 7838.7067
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.45 |  | 0.45 |  | 0.46 |  | 0.46 |  | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.1 |  | 18.9 |  | 19.2 |  | 19.5 |  | 19.9 |  | 19.8
| LIQUID LEVEL | mm | mm |  | 199.6 |  | 126.4 |  | 206.6 |  | 209.6 |  | 163 |  | 195.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.87 |  | 5.4 |  | 5.73 |  | 5.89 |  | 5.65 |  | 5.57
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 11
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-11
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 70.6 |  | 80 | 75.2 | 74 |  | 71.4 |  | 75.6 | 74.5 | 73.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 |  | 0.1 |  | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.7 |  | 76.2 | 71.5 | 69 |  | 67.8 |  | 71 | 69.9 | 67.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.4 |  | 68.8 | 63.7 | 63.6 |  | 66.3 |  | 73.4 | 73.5 | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.2 |  | 50.9 | 39.5 | 39.9 |  | 33.9 |  | 52.3 | 42 | 42.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 117.2 |  | 118.1 | 116.2 | 116.7 |  | 113.9 |  | 118.6 | 118.5 | 186.2
| INPUT | Kw | 1194kW |  | 1147 |  | 1194 | 1186 | 1181 |  | 1161 |  | 1208 | 1205 | 1182
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49489.5 |  | 50709 | 48361.3 | 48352.8 |  | 50742 |  | 49931.3 | 50085.9 | 50077.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.5 |  | 59.4 | 57.5 | 57.5 |  | 57.4 |  | 58.7 | 59.1 | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.52 |  | 0.48 | 0.5 | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 44.8 | 45.1 | 45 |  | 44.9 |  | 44.8 | 45.1 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.23 | 0.23 |  | 0.22 |  | 0.23 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.3 | 4 | 4.2 |  | 3.9 |  | 4.6 | 4.7 | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 |  | 2.5 | 3.2 | 3.5 |  | 2.8 |  | 3.6 | 3.8 | 3.5
| APPROACH TEMP | CELCIUS | C | 0 | 0.3 | 0 | 1.4 | 0.7 | 1 | 0 | 1 | 0 | 0.2 | 1.1 | 0.4
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 648.08 |  | 640.32 | 639.3 | 639.92 |  | 645.04 |  | 636.64 | 648.2 | 640.32
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.7 |  | 12.3 | 13.1 | 13.1 |  | 13.1 |  | 12.6 | 13.5 | 12.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.3 |  | 3.9 | 3.9 | 4.5 |  | 3.8 |  | 3.8 | 4.9 | 3.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.4 | 0 | 8.4 | 9.2 | 8.6 | 0 | 9.3 | 0 | 8.8 | 8.6 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6286.2263 | 0 | 6210.9561 | 6791.6397 | 6354.8637 | 0 | 6927.1039 | 0 | 6469.321 | 6437.0901 | 6210.9561
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.84 | 0.82 | 0.82 |  | 0.82 |  | 0.8 | 0.83 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.1 |  | 36.6 | 35.9 | 36.4 |  | 36.4 |  | 35.9 | 35.9 | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 37.1 | 36.6 | 36.4 |  | 36.6 |  | 35.5 | 36.8 | 36.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.6 | 0 | 4 | 2.4 | 3 | 0 | 3.3 | 0 | 2.3 | 3.1 | 3.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.9 |  | 27.8 | 28.7 | 27.9 |  | 27.5 |  | 27.6 | 28.3 | 28
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.8 |  | 33.1 | 34.2 | 33.4 |  | 33.3 |  | 33.2 | 33.7 | 33.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.9 | 0 | 5.3 | 5.5 | 5.5 | 0 | 5.8 | 0 | 5.6 | 5.4 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1098.58 |  | 1163.82 | 1298.2 | 1186.5 |  | 1164.52 |  | 1139.32 | 1289.3 | 1179.5
| HEAT CAPACITY | kW | 8226.9 | 0 | 7484.552 | 0 | 7122.6859 | 8244.9192 | 7535.5081 | 0 | 7799.3256 | 0 | 7367.4273 | 8039.515 | 7491.0508
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.45 | 0.46 |  | 0.46 |  | 0.46 | 0.47 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 |  | 19.5 | 19.2 | 19.7 |  | 19.7 |  | 19.4 | 20 | 20.1
| LIQUID LEVEL | mm | mm |  | 201 |  | 122.6 | 197.9 | 202.2 |  | 208 |  | 167.4 | 193.5 | 186.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.62 |  | 5.36 | 5.68 | 5.66 |  | 5.65 |  | 5.45 | 5.32 | 5.23
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 12
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-12
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 72.1 | 73.4 | 83.6 |  | 74.3 |  | 76.5 | 75.8 | 78.2 |  | 76.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.6 | 70.3 | 80.2 |  | 68.9 |  | 71.2 | 71.4 | 73.4 |  | 70.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 65.3 | 71.2 | 66.6 |  | 63.7 |  | 66.8 | 75.4 | 71.1 |  | 70.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 39.4 | 54.6 | 54.3 |  | 39 |  | 35 | 45.9 | 89.6 |  | 41.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.1 | 114.2 | 118.4 |  | 115.5 |  | 116.7 | 112.2 | 117.5 |  | 117.8
| INPUT | Kw | 1194kW |  | 1142 | 1150 | 1197 |  | 1172 |  | 1183 | 1187 | 1197 |  | 1191
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49498.5 | 50727.3 | 50718.3 |  | 48376.5 |  | 50750.2 | 49949.6 | 49940.7 |  | 50094.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 | 58.9 | 58.9 |  | 57.8 |  | 58.6 | 58.5 | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.48 |  | 0.56 |  | 0.52 | 0.47 | 0.47 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 | 45.1 | 45.1 |  | 45.1 |  | 45.5 | 45.4 | 44.9 |  | 45.3
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.22 | 0.22 | 0.21 |  | 0.22 |  | 0.22 | 0.23 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 3.9 | 3.5 | 2.5 |  | 4 |  | 3.7 |  | 3.8 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.2 | 2.7 | 1.8 |  | 3.2 |  | 2.7 | 3.1 | 2.5 |  | 3.2
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 2.1 | 2.1 | 0 | 1.2 | 0 | 1.1 | 1.2 | 1.4 | 0 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 641.5 | 655.52 | 640.6 |  | 639.9 |  | 624.7 | 636.24 | 640.4 |  | 640.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13 | 13.1 | 12.3 |  | 12.9 |  | 13.2 | 13.2 | 12.6 |  | 12.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.1 | 4.8 | 3.9 |  | 4.4 |  | 3.8 | 4.3 | 3.9 |  | 3.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.9 | 8.3 | 8.4 | 0 | 8.5 | 0 | 9.4 | 8.9 | 8.7 | 0 | 8.3
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6592.7829 | 6282.6975 | 6213.6721 | 0 | 6280.7737 | 0 | 6780.8083 | 6538.7252 | 6433.5797 | 0 | 6142.5751
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.79 | 0.83 | 0.82 |  | 0.81 |  | 0.82 | 0.79 | 0.76 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.2 | 35.7 | 35.6 |  | 35.2 |  | 35.3 |  | 34.6 |  | 35.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.6 | 36.7 | 36.5 |  | 36 |  | 36.8 | 35.2 | 35.1 |  | 63.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.1 | 4.1 | 3.7 | 0 | 2.4 | 0 | 3.5 | 2.5 | 1.7 | 0 | 30
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.4 | 27.8 | 27.5 |  | 27.5 |  | 27.5 | 27.6 | 27.3 |  | 27.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.5 | 32.6 | 32.8 |  | 33.6 |  | 33.3 | 32.7 | 33.4 |  | 33.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 6.1 | 4.8 | 5.3 | 0 | 6.1 | 0 | 5.8 | 5.1 | 6.1 | 0 | 5.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1156.9 | 1300.18 | 1155.5 |  | 1178.9 |  | 1153.8 | 1282.12 | 1132.1 |  | 1168.4
| HEAT CAPACITY | kW | 8226.9 | 0 | 8149.0647 | 7206.5404 | 7071.7667 | 0 | 8304.03 | 0 | 7727.5289 | 7550.5912 | 7974.3764 | 0 | 7960.2309
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.45 | 0.46 | 0.44 |  | 0.45 |  | 0.45 | 0.44 | 0.44 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.2 | 19.2 | 18.4 |  | 18.9 |  | 19.1 | 18.4 | 18.2 |  | 19.3
| LIQUID LEVEL | mm | mm |  | 197.9 | 131.2 | 125.2 |  | 206.3 |  | 200.8 | 153.6 | 157.2 |  | 196.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.6 | 5.73 | 5.72 |  | 5.78 |  | 5.75 | 5.89 | 5.75 |  | 5.59
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 13
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-13
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 66.6 |  | 82 | 74.6 | 73.4 | 70.5 | 76.5 |  | 78.2 |  | 76.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 62.7 |  | 78.3 | 71 | 58.2 | 67.5 | 71.2 |  | 73.4 |  | 70.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.9 |  | 66.8 | 64.6 | 63.9 | 66.2 | 66.8 |  | 71.1 |  | 70.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 40.6 |  | 54.5 | 39.2 | 38.5 | 33.8 | 35 |  | 89.6 |  | 41.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 113.9 |  | 117.7 | 115.5 | 116.1 | 111.9 | 116.7 |  | 117.5 |  | 117.8
| INPUT | Kw | 1194kW |  | 1122 |  | 1197 | 1180 | 1182 | 1147 | 1183 |  | 1197 |  | 1191
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49508 |  | 50737.8 | 48395.1 | 48386.1 | 50768.8 | 50759.8 |  | 49962.9 |  | 50104.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59.1 | 57.4 | 57.5 | 57.2 | 58.6 |  | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.48 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.47 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 44.7 | 45.1 | 44.9 | 45.1 | 45.5 |  | 44.9 |  | 45.3
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.22 | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3 | 4.1 | 4 | 3.8 | 3.7 |  | 3.8 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.7 |  | 2 | 3.2 | 3.2 | 3.2 | 2.7 |  | 2.5 |  | 3.2
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 |  | 2.4 | 1.2 | 1.2 | 0.5 | 1.1 |  | 1.4 | 0 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 669.9 |  | 652.5 | 627.44 | 651.14 | 624.32 | 624.1 |  | 654.9 |  | 645.8
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13 | 13.6 | 12.9 | 13.2 | 13.2 |  | 12.6 |  | 12.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.4 | 4.4 | 4.4 | 3.7 | 3.8 |  | 3.9 |  | 3.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.9 |  | 8.6 | 9.2 | 8.5 | 9.5 | 9.4 |  | 8.7 | 0 | 8.3
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6884.6536 |  | 6479.7921 | 6665.6443 | 6391.097 | 6848.776 | 6774.2956 |  | 6579.2494 | 0 | 6189.5381
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 |  | 0.83 | 0.82 | 0.81 | 0.81 | 0.82 |  | 0.76 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.5 |  | 36.1 | 35.6 | 35.2 | 35.4 | 35.3 |  | 34.6 |  | 35.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.9 |  | 36.9 | 36.5 | 36 | 36.1 | 36.8 |  | 35.1 |  | 63.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.1 |  | 3.5 | 3.2 | 2.4 | 3.4 | 3.5 |  | 1.7 | 0 | 30
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.9 |  | 27.8 | 27.8 | 27.5 | 27.5 | 27.5 |  | 27.3 |  | 27.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.8 |  | 33.4 | 33.3 | 33.6 | 32.7 | 33.3 |  | 33.4 |  | 33.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 4.9 |  | 5.6 | 5.5 | 6.1 | 5.2 | 5.8 |  | 6.1 | 0 | 5.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1154.4 |  | 1152.6 | 1292.34 | 1176.4 | 1300.32 | 1155.6 |  | 1134.7 |  | 1170.3
| HEAT CAPACITY | kW | 8226.9 | 0 | 6531.8245 |  | 7453.3025 | 8207.7021 | 8286.4203 | 7807.9261 | 7739.5843 |  | 7992.6905 | 0 | 7973.1755
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 | 0.45 | 0.45 | 0.45 | 0.45 |  | 0.44 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.6 |  | 18.9 | 19 | 18.9 | 19.2 | 19.1 |  | 18.2 |  | 19.3
| LIQUID LEVEL | mm | mm |  | 199.7 |  | 127.9 | 195 | 206.3 | 209 | 200.8 |  | 157.2 |  | 196.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.86 |  | 5.81 | 5.77 | 5.78 | 5.71 | 5.75 |  | 5.75 |  | 5.59
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 14
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-14
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 70.6 | 68.8 | 80 |  | 74 |  | 71.4 |  | 75.6 | 74 | 73.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 | 0 | 0 |  | 0 |  | 0.1 |  | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.7 | 64.9 | 76.2 |  | 69 |  | 67.8 |  | 71 | 68.1 | 67.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.4 | 70.8 | 68.8 |  | 63.6 |  | 66.3 |  | 73.4 | 73.3 | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.2 | 54.6 | 50.9 |  | 39.9 |  | 33.9 |  | 52.3 | 42 | 42.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 117.2 | 110.3 | 118.1 |  | 116.7 |  | 113.9 |  | 118.6 | 116.9 | 186.2
| INPUT | Kw | 1194kW |  | 1147 | 1128 | 1194 |  | 1181 |  | 1161 |  | 1208 | 1191 | 1182
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49517.5 | 50756 | 50747 |  | 48404 |  | 50783 |  | 49980.7 | 50122.8 | 50113.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.5 | 59.1 | 59.4 |  | 57.5 |  | 57.4 |  | 58.7 | 58.9 | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.5 | 0.49 |  | 0.59 |  | 0.52 |  | 0.48 | 0.5 | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 | 44.7 | 44.8 |  | 45 |  | 44.9 |  | 44.8 | 45.2 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.22 | 0.22 |  | 0.23 |  | 0.22 |  | 0.23 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 | 4.2 | 3.3 |  | 4.2 |  | 3.9 |  | 4.6 | 4.8 | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 | 3.2 | 2.5 |  | 3.5 |  | 2.8 |  | 3.6 | 3.7 | 3.5
| APPROACH TEMP | CELCIUS | C | 0 | 0.3 | 2.1 | 1.4 |  | 1 | 0 | 1 | 0 | 0.2 | 1 | 0.4
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 648.08 | 646.7 | 640.32 |  | 639.92 |  | 645.04 |  | 636.64 | 637.6 | 640.32
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.7 | 13.7 | 12.3 |  | 13.1 |  | 13.1 |  | 12.6 | 13.6 | 12.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.3 | 5.5 | 3.9 |  | 4.5 |  | 3.8 |  | 3.8 | 4.7 | 3.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.4 | 8.3 | 8.4 |  | 8.6 | 0 | 9.3 | 0 | 8.8 | 8.9 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6286.2263 | 6282.6975 | 6210.9561 |  | 6354.8637 | 0 | 6927.1039 | 0 | 6469.321 | 6552.7021 | 6210.9561
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.83 | 0.84 |  | 0.82 |  | 0.82 |  | 0.8 | 0.82 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.1 | 36.1 | 36.6 |  | 36.4 |  | 36.4 |  | 35.9 | 36 | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 | 36.9 | 37.1 |  | 36.4 |  | 36.6 |  | 35.5 | 36.7 | 36.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.6 | 4.1 | 4 |  | 3 | 0 | 3.3 | 0 | 2.3 | 3 | 3.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.9 | 28.3 | 27.8 |  | 27.9 |  | 27.5 |  | 27.6 | 28.1 | 28
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.8 | 33.4 | 33.1 |  | 33.4 |  | 33.3 |  | 33.2 | 33.7 | 33.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.9 | 4.8 | 5.3 |  | 5.5 | 0 | 5.8 | 0 | 5.6 | 5.6 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1098.58 | 1226.2 | 1163.82 |  | 1186.5 |  | 1164.52 |  | 1139.32 | 1247.3 | 1179.5
| HEAT CAPACITY | kW | 8226.9 | 0 | 7484.552 | 7206.5404 | 7122.6859 |  | 7535.5081 | 0 | 7799.3256 | 0 | 7367.4273 | 8065.6813 | 7491.0508
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.46 | 0.46 |  | 0.46 |  | 0.46 |  | 0.46 | 0.47 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 | 19.7 | 19.5 |  | 19.7 |  | 19.7 |  | 19.4 | 20 | 20.1
| LIQUID LEVEL | mm | mm |  | 201 | 119.8 | 122.6 |  | 202.2 |  | 208 |  | 167.4 | 196.4 | 186.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.62 | 5.41 | 5.36 |  | 5.66 |  | 5.65 |  | 5.45 | 5.45 | 5.23
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 15
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-15
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 68.9 | 68.2 |  | 77.2 |  | 74.1 | 72.4 | 73.1 |  | 76.1 |  | 73.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 65.5 | 62.7 |  | 67.4 |  | 68.9 | 69.9 | 68.3 |  | 70.4 |  | 67.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 65.8 | 67.1 |  | 67.4 |  | 64.1 | 65.5 | 65.9 |  | 72 |  | 71.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 38.5 | 39.5 |  | 54.2 |  | 41.4 | 30.6 | 35.6 |  |  |  | 42.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 117.5 | 115.5 |  | 115.6 |  | 117.7 | 115 | 115 |  | 117.7 |  | 117.7
| INPUT | Kw | 1194kW | 1163 | 1123 |  | 1167 |  | 1182 | 1172 | 1157 |  | 1188 |  | 1186
COMPRESSOR | RUNNING TIME | Hr | NA | 49536.3 | 49526.9 |  | 50771.5 |  | 48413.6 | 50804 | 50793.6 |  | 49982.5 |  | 50134.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 57.9 |  | 59.1 |  | 57.7 | 57.4 | 57.1 |  | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 |  | 0.48 |  | 0.59 | 0.52 | 0.52 |  |  |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 45 |  | 45 |  | 45 | 44.9 | 45 |  | 44.9 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.26 |  | 0.21 |  | 0.22 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.5 | 4 |  | 3.1 |  | 4 | 3.8 | 3.5 |  | 4.1 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 4 | 3.5 |  | 2.1 |  | 3.3 | 2.8 | 3.5 |  | 3.5 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 1 | 0.9 | 0 | 2.5 | 0 | 0.8 | 1.5 | 0.3 | 0 | 0.8 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 694.4 | 664.6 |  | 646.4 |  | 644.4 | 631 | 626.3 |  | 651.3 |  | 641.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.5 | 13.5 |  | 13.4 |  | 13.2 | 13.5 | 13.1 |  | 13.3 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.8 | 4.4 |  | 4.6 |  | 4.1 | 4.3 | 3.8 |  | 4.3 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.9 | 9.1 | 0 | 8.8 | 0 | 9.1 | 9.2 | 9.3 | 0 | 9 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 6643.1409 | 6983.6721 | 0 | 6568.4988 | 0 | 6771.4088 | 6981.8014 | 6725.8545 | 0 | 6768.7067 | 0 | 6300.4042
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.8 |  | 0.82 |  | 0.81 | 0.79 | 0.8 |  | 0.78 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.5 | 35 |  | 35.7 |  | 35.4 | 34.5 | 35.2 |  | 34.6 |  | 35.5
| SATURATED TEMEPRATURE | CELCIUS | C | 35.2 | 35.6 |  | 36.5 |  | 36.1 | 35.3 | 35.7 |  | 35 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0.5 | 2.2 | 0 | 3.6 | 0 | 2.4 | 2.5 | 2.5 | 0 | 1.6 | 0 | 3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.4 | 27.6 |  | 27.5 |  | 27.6 | 27.5 | 27.5 |  | 27.2 |  | 27.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.7 | 33.4 |  | 32.9 |  | 33.7 | 32.8 | 33.2 |  | 33.4 |  | 33.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.3 | 5.8 | 0 | 5.4 | 0 | 6.1 | 5.3 | 5.7 | 0 | 6.2 | 0 | 6.1
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1296.5 | 1161.1 |  | 1151.8 |  | 1181.6 | 1295.7 | 1153.7 |  | 1137 |  | 1168.6
| HEAT CAPACITY | kW | 8226.9 | 7922.0924 | 7776.4203 | 0 | 7182.1247 | 0 | 8323.0485 | 7895.5312 | 7593.6374 | 0 | 8140.1848 | 0 | 8231.4781
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.46 |  | 0.44 |  | 0.45 | 0.45 | 0.45 |  | 0.44 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 20.2 | 19.5 |  | 18.5 |  | 19.2 | 18.8 | 19 |  | 18.5 |  | 19.7
| LIQUID LEVEL | mm | mm | 202.2 | 198.6 |  | 123.8 |  | 204.2 | 213.5 | 207.1 |  | 157.4 |  | 196
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.54 | 5.79 |  | 5.43 |  | 5.73 | 5.57 | 5.95 |  | 5.74 |  | 5.42
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 16
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-16
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  |  | 76.6 | [5 empty] | 76.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  |  | 0 | [5 empty] | 0
OPENING OF 2nd VANE |  | % | 0~100% |  |  | 74.3 | [5 empty] | 71.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  |  | 67.9 | [5 empty] | 72.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  |  | 49.7 | [5 empty] | 53.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  |  | 6.6 | [5 empty] | 6.6
| CURRENT | A | ≤115A |  |  | 117.2 | [5 empty] | 120.6
| INPUT | Kw | 1194kW |  |  | 1189 | [5 empty] | 1226
COMPRESSOR | RUNNING TIME | Hr | NA |  |  | 50796.1 | [5 empty] | 50000.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  |  | 59.4 | [5 empty] | 58.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  |  | 0.49 | [5 empty] | 0.82
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  |  | 44.8 | [5 empty] | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  |  | 0.22 | [5 empty] | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  |  | 3.6 | [5 empty] | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  |  | 2.7 | [5 empty] | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  |  | 683.4 | [5 empty] | 691
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  |  | 13.4 | [5 empty] | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  |  | 5.3 | [5 empty] | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 0 | 8.1 | 0 | 0 | 0 | 0 | 0 | 8.7 | 0 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 0 | 6392.0785 | 0 | 0 | 0 | 0 | 0 | 6941.9169 | 0 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  |  | 0.86 | [5 empty] | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  |  | 37.3 | [5 empty] | 36.1
| SATURATED TEMEPRATURE | CELCIUS | C |  |  | 38.2 | [5 empty] | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  |  | 29.7 | [5 empty] | 29.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  |  | 34.5 | [5 empty] | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  |  | 1292 | [5 empty] | 1286.7
| HEAT CAPACITY | kW | 8226.9 | 0 | 0 | 7161.2009 | 0 | 0 | 0 | 0 | 0 | 8023.3025 | 0 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  |  | 0.47 | [5 empty] | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  |  | 19.9 | [5 empty] | 19.8
| LIQUID LEVEL | mm | mm |  |  | 124.2 | [5 empty] | 157.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  |  | 5.15 | [5 empty] | 5.24
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 17
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-17
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 71.9 |  | 76 | 75.3 | 74 |  | 69.7 |  | 76.5 | 75.9 | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.4 |  | 71.3 | 69.6 | 69.1 |  | 65.3 |  | 71.6 | 70.4 | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.8 |  | 70.6 | 62.5 | 63.8 |  | 65.2 |  | 74.2 | 70.1 | 73.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.3 |  | 52.2 | 38.2 | 38.2 |  | 32.1 |  | 53.5 | 41.2 | 42
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 117.5 |  | 115.6 | 118.5 | 116.4 |  | 112.3 |  | 118.3 | 120 | 118.5
| INPUT | Kw | 1194kW |  | 1158 |  | 1171 | 1215 | 1182 |  | 1140 |  | 1202 | 1218 | 1205
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49553.1 |  | 50800.2 | 48442.3 | 48432.2 |  | 50826.3 |  | 50015.4 | 50163 | 50153
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 59 |  | 58.9 | 58 | 57.8 |  | 57.2 |  | 58.5 | 59.1 | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 | 0.59 | 0.59 |  | 0.52 |  | 0.47 | 0.5 | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 |  | 45.2 | 44.9 | 44.8 |  | 45.2 |  | 45.1 | 44.9 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.23 | 0.23 |  | 0.22 |  | 0.22 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.5 | 4.6 | 4.2 |  | 3.7 |  | 4.1 | 4.7 | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.7 | 3.7 | 3.5 |  | 2.7 |  | 3.3 | 3.7 | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | 2.1 | 0.8 | 0.7 | 0 | 1.1 | 0 | 1.1 | 1.2 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 673 |  | 652.6 | 681.5 | 634.3 |  | 643.3 |  | 652.8 | 676.1 | 643
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.4 |  | 13.6 | 13 | 13.4 |  | 12.8 |  | 13.6 | 13 | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 |  | 4.8 | 4.5 | 4.2 |  | 3.8 |  | 4.4 | 4.9 | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.6 | 0 | 8.8 | 8.5 | 9.2 | 0 | 9 | 0 | 9.2 | 8.1 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6683.3718 | 0 | 6631.5012 | 6689.0878 | 6738.5219 | 0 | 6685.5658 | 0 | 6935.0577 | 6323.7991 | 6385.4503
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.84 | 0.85 | 0.82 |  | 0.81 |  | 0.82 | 0.85 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 |  | 36.2 | 36.9 | 36 |  | 35.7 |  | 35.3 | 37 | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 37.2 | 37.7 | 36.7 |  | 36.2 |  | 35.7 | 37.8 | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.1 | 0 | 3.8 | 2.5 | 2.4 | 0 | 2.5 | 0 | 1.6 | 3.1 | 3.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28 |  | 28.2 | 29.7 | 28.3 |  | 28.2 |  | 28 | 29.3 | 27.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.3 |  | 33.4 | 35.2 | 34.3 |  | 33.7 |  | 34.1 | 34.7 | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 6.3 | 0 | 5.2 | 5.5 | 6 | 0 | 5.5 | 0 | 6.1 | 5.4 | 6
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1155.8 |  | 1149.9 | 1294.2 | 1177.2 |  | 1151.4 |  | 1138.6 | 1278.1 | 1165.7
| HEAT CAPACITY | kW | 8226.9 | 0 | 8408.2448 | 0 | 6904.7113 | 8219.515 | 8156.1201 | 0 | 7312.5866 | 0 | 8020.1617 | 7969.6767 | 8076.4434
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.47 | 0.46 |  | 0.46 |  | 0.45 | 0.48 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.9 |  | 19.4 | 20 | 19.6 |  | 19.5 |  | 19.1 | 20.5 | 20.1
| LIQUID LEVEL | mm | mm |  | 196.9 |  | 120.4 | 205.6 | 205 |  | 195.4 |  | 159.9 | 201.1 | 195.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.6 |  | 5.5 | 5.19 | 5.72 |  | 5.72 |  | 5.64 | 4.95 | 5.26
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 18
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-18
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 69.1 |  | 75.3 |  | 72.6 |  | 70.5 |  | 73.7 |  | 67.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.5 |  | 0 |  | 0 |  | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.2 |  | 72.7 |  | 67.2 |  | 67.2 |  | 68.5 |  | 35.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 65.2 |  | 66.9 |  | 62.6 |  | 64.9 |  | 71.2 |  | 69.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 33.6 |  | 47.7 |  | 36.5 |  | 28.7 |  | 43.1 |  | 35.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.4 |  | 115.7 |  | 116.7 |  | 114.4 |  | 112.2 |  | 113.9
| INPUT | Kw | 1194kW |  | 1119 |  | 1157 |  | 1167 |  | 1157 |  | 1180 |  | 1145
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49562.4 |  | 50809.9 |  | 48452.3 |  | 50836 |  | 50025 |  | 50176.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 59.8 |  | 59.3 |  | 57.7 |  | 57.5 |  | 53.3 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 |  | 0.59 |  | 0.52 |  | 0.47 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 46.1 |  | 44.8 |  | 45.8 |  | 45 |  | 44.6 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.2 |  | 3.6 |  | 4.1 |  | 4 |  | 4.1 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.6 |  | 2.3 |  | 3.4 |  | 3 |  | 3 |  | 3.5
| APPROACH TEMP | CELCIUS | C | 0 | 0.7 | 0 | 2 | 0 | 1.2 | 0 | 1 | 0 | 1 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 653.76 |  | 641.92 |  | 639.92 |  | 641.2 |  | 636.96 |  | 637.68
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.8 |  | 12.4 |  | 13.2 |  | 13.1 |  | 12.8 |  | 12.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.3 |  | 4.3 |  | 4.6 |  | 4 |  | 4 |  | 4.4
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.5 | 0 | 8.1 | 0 | 8.6 | 0 | 9.1 | 0 | 8.8 | 0 | 8.2
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6416.8129 | 0 | 6004.1016 | 0 | 6354.8637 | 0 | 6737.7829 | 0 | 6472.5727 | 0 | 6038.0785
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 |  | 0.84 |  | 0.84 |  | 0.81 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 |  | 36.6 |  | 36.6 |  | 36.6 |  | 35.9 |  | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.8 |  | 37.6 |  | 37.3 |  | 37 |  | 36.2 |  | 37.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.7 | 0 | 4 | 0 | 3.2 | 0 | 3.2 | 0 | 2.4 | 0 | 3.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.4 |  | 28.3 |  | 28.4 |  | 28.2 |  | 28.3 |  | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.1 |  | 33.6 |  | 34.1 |  | 33.8 |  | 33.8 |  | 34
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.7 | 0 | 5.3 | 0 | 5.7 | 0 | 5.6 | 0 | 5.5 | 0 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1153.46 |  | 1150.38 |  | 1170.96 |  | 1152.62 |  | 1131.34 |  | 1160.6
| HEAT CAPACITY | kW | 8226.9 | 0 | 7592.0577 | 0 | 7040.4319 | 0 | 7707.2425 | 0 | 7453.4319 | 0 | 7185.1848 | 0 | 7371.0162
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 |  | 0.46 |  | 0.47 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 |  | 19.5 |  | 19.9 |  | 19.9 |  | 19.9 |  | 20.3
| LIQUID LEVEL | mm | mm |  | 200.8 |  | 124.3 |  | 207.6 |  | 220.1 |  | 158.3 |  | 201.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.86 |  | 5.4 |  | 5.61 |  | 5.6 |  | 5.51 |  | 5.14
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 19
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-19
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK |  | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.3 | 80.4 | 80.5 |  | 75.5 |  | 73.5 | 77.3 | 76.7 |  | 74.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.8 | 76.4 | 76.9 |  | 69.8 |  | 68.5 | 72.1 | 71.9 |  | 69.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.9 | 68 | 69.9 |  | 64.8 |  | 66.2 | 72.2 | 74.4 |  | 73.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.4 | 51.8 | 52.6 |  | 41.1 |  | 34.9 | 53.7 | 65.3 |  | 45.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.2 | 117.2 | 117.2 |  | 115.8 |  | 114.2 | 118.8 | 112.5 |  | 117.3
| INPUT | Kw | 1194kW |  | 1137 | 1190 | 1192 |  | 1180 |  | 1161 | 1209 | 1200 |  | 1193
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49580.1 | 50829.8 | 50820 |  | 48467.2 |  | 50854.1 | 50044.8 | 50034.9 |  | 50186.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 | 59.2 | 59.3 |  | 57.7 |  | 57.2 | 58.6 | 58.6 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.49 | 0.48 |  | 0.59 |  | 0.44 | 0.45 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.7 | 44.9 | 44.7 |  | 44.9 |  | 44.8 | 44.9 | 44.9 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.22 |  | 0.23 |  | 0.22 | 0.23 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.1 | 3.1 | 3.3 |  | 4.1 |  | 3.6 | 4.2 | 4.4 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 | 2.1 | 2.3 |  | 3.2 |  | 2.7 | 3.3 | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C |  | 0.8 | 2.7 | 1.9 | 0 | 1.3 | 0 | 1.1 | 1.1 | 0.8 | 0 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 649.76 | 677.4 | 639.68 |  | 640.56 |  | 625.36 | 689.7 | 635.6 |  | 638
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.1 | 13 | 12.6 |  | 13.3 |  | 13.2 | 13 | 12.9 |  | 12.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 | 4.8 | 4.2 |  | 4.5 |  | 3.8 | 4.4 | 4.1 |  | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8.5 | 8.2 | 8.4 | 0 | 8.8 | 0 | 9.4 | 8.6 | 8.8 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW |  | 6377.552 | 6414.1801 | 6204.7483 | 0 | 6509.1547 | 0 | 6787.9723 | 7486.351 | 6458.7529 | 0 | 6262.1247
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.84 | 0.85 |  | 0.84 |  | 0.84 | 8.2 | 0.82 |  | 0.85
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.3 | 36.5 | 36 |  | 35.6 |  | 35.5 | 35.3 | 36.2 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.9 | 37.4 | 37.7 |  | 37.3 |  | 37.1 | 35.7 | 35.4 |  | 37.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 |  | 2.8 | 3.7 | 4.1 | 0 | 3.2 | 0 | 3.3 | 1.7 | 1.6 | 0 | 3.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.3 | 28.8 | 28.2 |  | 28.3 |  | 28.1 | 28.5 | 28.3 |  | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.1 | 33.7 | 33.6 |  | 34.1 |  | 33.8 | 34 | 33.8 |  | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.8 | 4.9 | 5.4 | 0 | 5.8 | 0 | 5.7 | 5.5 | 5.5 | 0 | 5.6
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1115.66 | 1285.2 | 1155.42 |  | 1176.56 |  | 1155.98 | 1279.2 | 1137.08 |  | 1169.56
| HEAT CAPACITY | kW | 8226.9 |  | 7472.0878 | 7271.9169 | 7204.6975 | 0 | 7879.963 | 0 | 7608.6443 | 8124.2494 | 7221.6397 | 0 | 7562.9746
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.45 | 0.45 | 0.45 |  | 0.46 |  | 0.46 | 0.45 | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.1 | 19 | 18.9 |  | 19.2 |  | 19.5 | 18.9 | 19.9 |  | 19.8
| LIQUID LEVEL | mm | mm |  | 199.6 | 129.9 | 126.4 |  | 206.6 |  | 209.6 | 158.7 | 163 |  | 195.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.87 | 5.13 | 5.4 |  | 5.73 |  | 5.89 | 5.26 | 5.65 |  | 5.57
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 20
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-20
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 71 |  | 80.3 | 74.9 | 70.8 |  | 74.6 |  | 75.2 | 73.7 | 74
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 |  | 0.1 |  | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.2 |  | 76.3 | 70.4 | 67.1 |  | 69.9 |  | 70.5 | 71.2 | 69.4
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.6 |  | 65.5 | 64.1 | 62.6 |  | 65.9 |  | 71.8 | 72.7 | 68.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.9 |  | 50.1 | 40.9 | 36.9 |  | 32.8 |  | 52.5 | 41.4 | 38.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 116.1 |  | 115.6 | 117.5 | 114.3 |  | 116.3 |  | 116.9 | 119.6 | 116.9
| INPUT | Kw | 1194kW |  | 1150 |  | 1171 | 1186 | 1173 |  | 1181 |  | 1186 | 1205 | 1186
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49589.8 |  | 50844.5 | 48485.6 | 48477.2 |  | 50864.2 |  | 50053.5 | 50205.2 | 50196.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.1 | 57.4 | 57.7 |  | 57.2 |  | 58.5 | 59 | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.48 | 0.59 | 0.59 |  | 0.52 |  | 0.57 | 0.5 | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 |  | 44.9 | 44.9 | 44.9 |  | 44.9 |  | 45.1 | 45.2 | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.25 |  | 0.2 | 0.23 | 0.22 |  | 0.22 |  | 0.22 | 0.23 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 |  | 2.5 | 4 | 4.2 |  | 3.7 |  | 3.8 | 4.7 | 4
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.3 |  | 1.6 | 3.3 | 3.2 |  | 2.7 |  | 2.7 | 3.8 | 3
| APPROACH TEMP | CELCIUS | C |  | 1 | 0 | 2.4 | 1.3 | 1.2 | 0 | 0.9 | 0 | 1.2 | 1 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 661.4 |  | 646.4 | 639.36 | 647.2 |  | 630.4 |  | 639.9 | 636.08 | 644.3
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.8 |  | 12.4 | 13.4 | 13.2 |  | 13 |  | 12.8 | 13.6 | 12.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.3 |  | 4 | 4.6 | 4.4 |  | 3.6 |  | 3.9 | 4.8 | 4.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8.5 | 0 | 8.4 | 8.8 | 8.8 | 0 | 3.6 | 0 | 8.9 | 8.8 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW |  | 6491.8014 | 0 | 6269.9307 | 6496.9607 | 6576.6282 | 0 | 2620.6005 | 0 | 6576.3395 | 6463.6305 | 6323.9607
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.84 | 0.83 | 0.82 |  | 0.82 |  | 0.86 | 0.84 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 34 |  | 36.3 | 36 | 36 |  | 36.2 |  | 35.3 | 36.1 | 36.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 37.2 | 36.8 | 36.7 |  | 36.6 |  | 35.7 | 37 | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 |  | 2.1 | 0 | 3.6 | 3.2 | 2.4 | 0 | 2.6 | 0 | 1.6 | 3.4 | 3.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.3 |  | 28.5 | 28.2 | 28.4 |  | 28.3 |  | 28.1 | 28.2 | 28.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.3 |  | 33.6 | 33.6 | 34.3 |  | 34 |  | 34.1 | 33.6 | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 6 | 0 | 5.1 | 5.4 | 5.9 | 0 | 5.7 | 0 | 6 | 5.4 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1150.1 |  | 1142.5 | 1289.12 | 1169.7 |  | 1150.6 |  | 1132.8 | 1279.32 | 1160
| HEAT CAPACITY | kW | 8226.9 |  | 7968.3603 | 0 | 6728.3487 | 8038.3926 | 7969.0878 | 0 | 7573.2333 | 0 | 7848.4988 | 7977.2841 | 7769.0531
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 | 0.46 | 0.46 |  | 0.46 |  | 0.45 | 0.47 | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.7 |  | 18.9 | 19.4 | 19.5 |  | 19.6 |  | 18.2 | 19.7 | 19.7
| LIQUID LEVEL | mm | mm |  | 201.7 |  | 129.4 | 190.7 | 207.9 |  | 220.7 |  | 170.1 | 196.1 | 195.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.72 |  | 5.36 | 5.71 | 5.59 |  | 5.83 |  | 5.69 | 5.39 | 5.19
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 21
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-21
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.4 | 68.1 | 79.1 |  | 65 | 70 | 70.5 |  | 69.6 |  | 72.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64 | 63.8 | 74.6 |  | 60.8 | 66.2 | 65 |  | 66 |  | 67.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.6 | 70.1 | 65.9 |  | 63.3 | 66.2 | 66.2 |  | 70.8 |  | 68.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.2 | 58.4 | 56.9 |  | 37.4 | 32.8 | 31.5 |  | 53.3 |  | 40
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115 | 109.8 | 115.3 |  | 109.1 | 111.5 | 112.3 |  | 112.4 |  | 115
| INPUT | Kw | 1194kW |  | 1119 | 1109 | 1164 |  | 1108 | 1131 | 1140 |  | 1137 |  | 1160
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49598.9 | 50862.8 | 50854.1 |  | 48499.8 | 50882.6 | 50874 |  | 50063.1 |  | 50215
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 | 58.9 | 58.8 |  | 58.1 | 57.2 | 57.3 |  | 58.5 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.48 |  | 0.58 | 0.54 | 0.52 |  | 0.47 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 | 45 | 44.8 |  | 45.7 | 45.2 | 45.1 |  | 44.9 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.22 | 0.22 | 0.21 |  | 0.22 | 0.23 | 0.22 |  | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 3.8 | 3.8 | 2.8 |  | 4.2 | 3.6 | 3.7 |  | 3.9 |  | 4
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.2 | 2.9 | 1.9 |  | 3.3 | 2.3 | 2.3 |  | 2.3 |  | 2.9
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 2.5 | 2.1 | 0 | 0.7 | 1.6 | 1.8 | 0 | 2.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 646.6 | 671.36 | 643.4 |  | 640.63 | 636 | 641.8 |  | 636.8 |  | 641.1
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.1 | 13.3 | 12.5 |  | 12.6 | 13.2 | 12.9 |  | 12.8 |  | 12.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.2 | 5.4 | 4 |  | 4 | 3.9 | 4.1 |  | 4.4 |  | 3.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.9 | 7.9 | 8.5 | 0 | 8.6 | 9.3 | 8.8 | 0 | 8.4 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6645.1963 | 6124.4157 | 6315.127 | 0 | 6361.9145 | 6830.0231 | 6521.7552 | 0 | 6176.8129 | 0 | 6292.552
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 | 0.82 | 0.82 |  | 0.8 | 0.8 | 0.8 |  | 0.76 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.1 | 35.3 | 35.7 |  | 35.1 | 35 | 35.2 |  | 34.5 |  | 35.6
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.6 | 36.3 | 36.5 |  | 35.7 | 35.6 | 35.7 |  | 34.8 |  | 36.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.2 | 4.3 | 3.6 | 0 | 2.4 | 3.5 | 2.5 | 0 | 1.6 | 0 | 3.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.4 | 27.1 | 27.4 |  | 27.6 | 27 | 27.4 |  | 27.3 |  | 27.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.4 | 32 | 32.9 |  | 33.3 | 32.1 | 33.2 |  | 33.2 |  | 33.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 6 | 4.9 | 5.5 | 0 | 5.7 | 5.1 | 5.8 | 0 | 5.9 | 0 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1157.1 | 1295.28 | 1147.4 |  | 1166.1 | 1292.9 | 1151.3 |  | 1138.1 |  | 1158.1
| HEAT CAPACITY | kW | 8226.9 | 0 | 8016.8591 | 7328.9515 | 7287.1824 | 0 | 7675.254 | 7614.0762 | 7710.7852 | 0 | 7753.7991 | 0 | 7622.5982
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.45 | 0.44 |  | 0.46 | 0.45 | 0.46 |  | 0.44 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.3 | 19.3 | 18.4 |  | 19.4 | 19 | 19.3 |  | 18.5 |  | 19.3
| LIQUID LEVEL | mm | mm |  | 203.4 | 121.6 | 128.6 |  | 205.5 | 216.7 | 209.6 |  | 158.2 |  | 196.4
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.6 | 5.43 | 5.41 |  | 5.76 | 5.85 | 5.69 |  | 5.72 |  | 5.36
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 22
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-22
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 67.6 | 81.9 | 74.2 |  | 72.9 |  | 73.4 | 77.9 | 74.3 |  | 72.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 | 0 | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 61.2 | 77.5 | 68.4 |  | 66.8 |  | 71.2 | 72.7 | 73.5 |  | 66.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69 | 70.6 | 70.8 |  | 63.7 |  | 65.2 | 74.5 | 68.7 |  | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 34.6 | 56.7 | 51.3 |  | 38.5 |  | 32.5 | 58.8 | 52.1 |  | 42
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.1 | 116.5 | 115.5 |  | 115.6 |  | 116.3 | 117.3 | 117.2 |  | 118
| INPUT | Kw | 1194kW |  | 1137 | 1183 | 1167 |  | 1176 |  | 1185 | 1191 | 1192 |  | 1199
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49068.1 | 50880.1 | 50871.7 |  | 48509.2 |  | 50893.6 | 50081.1 | 50072.7 |  | 50224.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 | 58.9 | 59.1 |  | 57.8 |  | 57.3 | 58.3 | 58.7 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.49 | 0.5 |  | 0.59 |  | 0.52 | 0.47 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 | 44.8 | 45 |  | 44.9 |  | 45 | 45.1 | 45.1 |  | 44.7
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.22 |  | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 | 3 | 3.9 |  | 4.4 |  | 3.8 | 4.2 | 4.4 |  | 5
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 | 2.1 | 3.1 |  | 3.5 |  | 2.7 | 3.5 | 3.2 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 2.7 | 2.2 | 0 | 0.8 | 0 | 1.3 | 1.1 | 1.2 | 0 | 1.3
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 642.9 | 674.8 | 644.6 |  | 637.9 |  | 636.5 | 688.8 | 642.6 |  | 631.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.9 | 13.2 | 13.9 |  | 13.2 |  | 13 | 13.2 | 13.4 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.9 | 4.8 | 5.3 |  | 4.3 |  | 4 | 4.6 | 4.4 |  | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9 | 8.4 | 8.6 | 0 | 8.9 | 0 | 9 | 8.6 | 9 | 0 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6681.4088 | 6545.4042 | 6401.3395 | 0 | 6555.7852 | 0 | 6614.8961 | 6840.2771 | 6678.291 | 0 | 6124.4342
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.82 | 0.85 |  | 0.84 |  | 0.83 | 0.7 | 0.81 |  | 0.85
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.4 | 35.7 | 36.9 |  | 36.7 |  | 36.7 | 34.3 | 36 |  | 37
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.9 | 36.6 | 37.8 |  | 37.3 |  | 37.1 | 34.8 | 36.3 |  | 37.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.2 | 4 | 3.7 | 0 | 2.4 | 0 | 2.6 | 1.9 | 1.7 | 0 | 3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.8 | 27.7 | 28.8 |  | 28.9 |  | 28.8 | 27.4 | 28.5 |  | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.7 | 32.6 | 34.1 |  | 34.9 |  | 34.5 | 32.9 | 34.6 |  | 34.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.9 | 4.9 | 5.3 | 0 | 6 | 0 | 5.7 | 5.5 | 6.1 | 0 | 6.1
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1155.9 | 1280 | 1142.9 |  | 1173.5 |  | 1153.9 | 1286.6 | 1139.7 |  | 1156.6
| HEAT CAPACITY | kW | 8226.9 | 0 | 7875.0693 | 7242.4942 | 6994.6536 | 0 | 8130.485 | 0 | 7594.9538 | 8171.2471 | 8027.9099 | 0 | 8146.9515
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 | 0.44 | 0.47 |  | 0.47 |  | 0.46 | 0.44 | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.5 | 18.6 | 20.2 |  | 20.2 |  | 19.7 | 18.5 | 19.5 |  | 20.6
| LIQUID LEVEL | mm | mm |  | 200.6 | 124.5 | 117.9 |  | 203.8 |  | 208.3 | 163.9 | 167 |  | 203.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.82 | 5.63 | 5.47 |  | 5.62 |  | 5.7 | 5.88 | 5.63 |  | 5.17
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 23
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-14
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 70.6 |  | 80 | 77 | 74 |  | 71.4 |  | 75.6 | 74.9 | 73.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 |  | 0.1 |  | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.7 |  | 76.2 | 71.4 | 69 |  | 67.8 |  | 71 | 69.3 | 67.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.4 |  | 68.8 | 64.1 | 63.6 |  | 66.3 |  | 73.4 | 72.5 | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.2 |  | 50.9 | 41.5 | 39.9 |  | 33.9 |  | 52.3 | 43.8 | 42.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 117.2 |  | 118.1 | 117 | 116.7 |  | 113.9 |  | 118.6 | 117.3 | 186.2
| INPUT | Kw | 1194kW |  | 1147 |  | 1194 | 1192 | 1181 |  | 1161 |  | 1208 | 1194 | 1182
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49077 |  | 50889 | 48527.1 | 48519 |  | 50903 |  | 50093 | 50242.8 | 50235
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.5 |  | 59.4 | 57.5 | 57.5 |  | 57.4 |  | 58.7 | 59 | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.52 |  | 0.48 | 0.5 | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  |  | 44.7 | 44.8 | 44.6 | 45 |  | 44.9 |  | 44.8 | 44.8 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  |  | 0.22 | 0.22 | 0.22 | 0.23 |  | 0.22 |  | 0.23 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  |  | 4.2 | 3.3 | 4 | 4.2 |  | 3.9 |  | 4.6 | 4.7 | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  |  | 3.2 | 2.5 | 3.2 | 3.5 |  | 2.8 |  | 3.6 | 3.8 | 3.5
| APPROACH TEMP | CELCIUS | C | 0 | 0.3 | 2.1 | 1.4 | 1.2 | 1 | 0 | 1 | 0 | 0.2 | 1 | 0.4
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  |  | 646.7 | 640.32 | 644.67 | 639.92 |  | 645.04 |  | 636.64 | 673 | 640.32
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  |  | 13.7 | 12.3 | 13.1 | 13.1 |  | 13.1 |  | 12.6 | 13.2 | 12.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  |  | 5.5 | 3.9 | 4 | 4.5 |  | 3.8 |  | 3.8 | 4.8 | 3.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.4 | 8.3 | 8.4 | 9.1 | 8.6 | 0 | 9.3 | 0 | 8.8 | 8.4 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6286.2263 | 6282.6975 | 6210.9561 | 6774.246 | 6354.8637 | 0 | 6927.1039 | 0 | 6469.321 | 6527.9446 | 6210.9561
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  |  | 0.83 | 0.84 | 0.82 | 0.82 |  | 0.82 |  | 0.8 | 0.82 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  |  | 36.1 | 36.6 | 35.7 | 36.4 |  | 36.4 |  | 35.9 | 35.7 | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  |  | 36.9 | 37.1 | 36.5 | 36.4 |  | 36.6 |  | 35.5 | 36.6 | 36.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.6 | 4.1 | 4 | 2.8 | 3 | 0 | 3.3 | 0 | 2.3 | 3.3 | 3.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  |  | 28.3 | 27.8 | 28.2 | 27.9 |  | 27.5 |  | 27.6 | 27.8 | 28
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  |  | 33.4 | 33.1 | 33.7 | 33.4 |  | 33.3 |  | 33.2 | 33.3 | 33.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.9 | 4.8 | 5.3 | 5.5 | 5.5 | 0 | 5.8 | 0 | 5.6 | 5.5 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  |  | 1226.2 | 1163.82 | 1288.5 | 1186.5 |  | 1164.52 |  | 1139.32 | 1266.9 | 1179.5
| HEAT CAPACITY | kW | 8226.9 | 0 | 7484.552 | 7206.5404 | 7122.6859 | 8183.3141 | 7535.5081 | 0 | 7799.3256 | 0 | 7367.4273 | 8046.1316 | 7491.0508
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  |  | 0.46 | 0.46 | 0.45 | 0.46 |  | 0.46 |  | 0.46 | 0.46 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  |  | 19.7 | 19.5 | 19.3 | 19.7 |  | 19.7 |  | 19.4 | 19.9 | 20.1
| LIQUID LEVEL | mm | mm |  |  | 119.8 | 122.6 | 200.7 | 202.2 |  | 208 |  | 167.4 | 203.8 | 186.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  |  | 5.41 | 5.36 | 5.64 | 5.66 |  | 5.65 |  | 5.45 | 5.17 | 5.23
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 24
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-24
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  |  |  |  | 74.9 |  | 71.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  |  |  |  | 0 |  | 0.1
OPENING OF 2nd VANE |  | % | 0~100% |  |  |  |  | 69.1 |  | 68.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  |  |  |  | 62.8 |  | 65.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  |  |  |  | 37.8 |  | 31.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  |  |  |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  |  |  |  | 117.4 |  | 114.4
| INPUT | Kw | 1194kW |  |  |  |  | 1198 |  | 1164
COMPRESSOR | RUNNING TIME | Hr | NA |  |  |  |  | 48551.5 |  | 50925.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  |  |  |  | 58 |  | 57.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  |  |  |  | 0.59 |  | 0.52
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  |  |  |  | 45.3 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  |  |  |  | 0.23 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  |  |  |  | 4.3 |  | 3.7
| SATURATION TEMPERATURE | CELCIUS | C |  |  |  |  | 3.4 |  | 2.6
| APPROACH TEMP | CELCIUS | C | 0 | 0 | 0 | 0 | 0.7 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  |  |  |  | 655.9 |  | 629.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  |  |  |  | 13 |  | 12.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  |  |  |  | 4.1 |  | 3.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 0 | 0 | 0 | 8.9 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 0 | 0 | 0 | 6740.7737 | 0 | 6473.5681 | 0 | 0 | 0 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  |  |  |  | 0.83 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  |  |  |  | 36.3 |  | 36.2
| SATURATED TEMEPRATURE | CELCIUS | C |  |  |  |  | 37.1 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 0 | 0 | 0 | 2.7 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  |  |  |  | 28.9 |  | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  |  |  |  | 34.4 |  | 34
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 0 | 0 | 0 | 5.5 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  |  |  |  | 1279.3 |  | 1290
| HEAT CAPACITY | kW | 8226.9 | 0 | 0 | 0 | 0 | 8124.8845 | 0 | 7745.9584 | 0 | 0 | 0 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  |  |  |  | 0.46 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  |  |  |  | 19.8 |  | 19.5
| LIQUID LEVEL | mm | mm |  |  |  |  | 203.6 |  | 200.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  |  |  |  | 5.54 |  | 5.7
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 25
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-25
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 69.4 | 77 | 74.2 |  | 73.6 |  | 71.5 | 80 | 72.8 |  | 71.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.4 | 0 | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.3 | 74.4 | 69.2 |  | 68.9 |  | 68.1 | 76.1 | 68.1 |  | 64.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.6 | 71.2 | 70.9 |  | 63.8 |  | 64.9 | 75.3 | 73.6 |  | 72.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.9 | 56.8 | 47.3 |  | 36.6 |  | 30.2 | 53 | 56.2 |  | 41.1
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.2 | 115.8 | 114.5 |  | 116.4 |  | 115.3 | 118.5 | 117.1 |  | 117.1
| INPUT | Kw | 1194kW |  | 1161 | 1169 | 1169 |  | 1189 |  | 1175 | 1217 | 1196 |  | 1189
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49635 | 50918 | 50908.5 |  | 48556 |  | 50932.7 | 50121.6 | 50112.1 |  | 50261.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.6 | 59.1 | 59.3 |  | 57.9 |  | 57.3 | 58.1 | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.49 | 0.49 |  | 0.59 |  | 0.52 | 0.48 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 | 44.8 | 44.9 |  | 44.9 |  | 44.8 | 45.9 | 45.1 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.22 | 0.22 |  | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.7 | 3.3 | 3.9 |  | 4.4 |  | 4 | 3.9 | 4.5 |  | 5.1
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.1 | 2.5 | 3 |  | 3.4 |  | 2.9 | 2.9 | 3.1 |  | 4.1
| APPROACH TEMP | CELCIUS | C | 0 | 1.1 | 2.1 | 2.3 | 0 | 0.8 | 0 | 1.3 | 1 | 1.7 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 681 | 677.2 | 655.3 |  | 638.5 |  | 635.4 | 636.88 | 660 |  | 648.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.6 | 12.6 | 13.6 |  | 13.1 |  | 13 | 13.3 | 13.8 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5.2 | 4.6 | 5.3 |  | 4.2 |  | 4.2 | 3.9 | 4.8 |  | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.4 | 8 | 8.3 | 0 | 8.9 | 0 | 8.8 | 9.4 | 9 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6605.5427 | 6255.8891 | 6280.5889 | 0 | 6561.9515 | 0 | 6456.7206 | 6913.0162 | 6859.1224 | 0 | 6439.0762
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.82 | 0.86 |  | 0.84 |  | 0.83 | 0.79 | 0.82 |  | 0.85
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.7 | 35.8 | 37.1 |  | 36.8 |  | 36.7 | 34.5 | 36 |  | 37
| SATURATED TEMEPRATURE | CELCIUS | C |  | 37.1 | 36.7 | 38 |  | 37.5 |  | 37.1 | 35.3 | 36.5 |  | 37.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.1 | 3.6 | 3.7 | 0 | 2.5 | 0 | 2.5 | 2.5 | 1.8 | 0 | 3.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.8 | 28.2 | 28.8 |  | 29 |  | 28.8 | 27.5 | 28.7 |  | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 35 | 33.1 | 34.3 |  | 35 |  | 34.6 | 32.8 | 34.7 |  | 34.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 6.2 | 4.9 | 5.5 | 0 | 6 | 0 | 5.8 | 5.3 | 6 | 0 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1155.1 | 1305.9 | 1140.2 |  | 1165.4 |  | 1148.4 | 1282.96 | 1138.9 |  | 1154
| HEAT CAPACITY | kW | 8226.9 | 0 | 8269.7691 | 7389.0416 | 7241.455 | 0 | 8074.3649 | 0 | 7691.3626 | 7851.8337 | 7890.7621 | 0 | 7728.8684
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 | 0.45 | 0.47 |  | 0.47 |  | 0.47 | 0.44 | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.6 | 18.8 | 20.3 |  | 20.2 |  | 20 | 18.4 | 19.7 |  | 20.8
| LIQUID LEVEL | mm | mm |  | 196.4 | 118.1 | 126.3 |  | 198.6 |  | 218.3 | 159.4 | 156.4 |  | 194.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.4 | 5.51 | 5.38 |  | 5.56 |  | 5.52 | 5.76 | 5.56 |  | 5.34
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 26
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-26
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 67.9 |  | 76.6 |  | 73.4 |  | 74 |  | 74 |  | 70.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 61.3 |  | 72.3 |  | 68.3 |  | 69.4 |  | 68.7 |  | 63.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.9 |  | 71.4 |  | 64.6 |  | 64.8 |  | 75.2 |  | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 35.4 |  | 48 |  | 36.7 |  | 30.9 |  | 52.8 |  | 41.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.2 |  | 117.1 |  | 118.1 |  | 116.6 |  | 117.9 |  | 116.1
| INPUT | Kw | 1194kW |  | 1120 |  | 1183 |  | 1196 |  | 1178 |  | 1195 |  | 1177
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49644.4 |  | 50927.8 |  | 48565.7 |  | 50942.4 |  | 50134.3 |  | 50271
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.6 |  | 59.2 |  | 57.6 |  | 57.2 |  | 58.6 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 |  | 0.53 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 44.8 |  | 44.7 |  | 45.8 |  | 45.1 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.24 |  | 0.22 |  | 0.23 |  | 0.22 |  | 0.23 |  | 0.24
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 |  | 3.7 |  | 4.4 |  | 3.8 |  | 4.7 |  | 5.1
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.2 |  | 2.9 |  | 3.6 |  | 2.7 |  | 3.5 |  | 4.1
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0 | 2.1 | 0 | 1.1 | 0 | 0.8 | 0 | 1.1 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 671.76 |  | 650.56 |  | 632.72 |  | 625.52 |  | 650.64 |  | 634.32
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.4 |  | 13.5 |  | 13.7 |  | 12.9 |  | 13.5 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 |  | 5 |  | 4.7 |  | 3.5 |  | 4.6 |  | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.4 | 0 | 8.5 | 0 | 9 | 0 | 9.4 | 0 | 8.9 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6515.9169 | 0 | 6385.4042 | 0 | 6575.612 | 0 | 6789.709 | 0 | 6686.7159 | 0 | 6226.0046
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 |  | 0.84 |  | 0.83 |  | 0.81 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.2 |  | 36.9 |  | 36.6 |  | 36.4 |  | 35.7 |  | 36.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.8 |  | 37.7 |  | 37.3 |  | 36.9 |  | 36.2 |  | 37.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 3 | 0 | 4.1 | 0 | 3.3 | 0 | 3.3 | 0 | 2.6 | 0 | 3.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.1 |  | 27.9 |  | 28 |  | 27.9 |  | 27.9 |  | 28.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.8 |  | 33.6 |  | 34 |  | 33.6 |  | 33.6 |  | 34
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.7 | 0 | 5.7 | 0 | 6 | 0 | 5.7 | 0 | 5.7 | 0 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1151.5 |  | 1134.28 |  | 1164.52 |  | 1145.06 |  | 1132.88 |  | 1149.82
| HEAT CAPACITY | kW | 8226.9 | 0 | 7579.157 | 0 | 7465.8152 | 0 | 8068.2679 | 0 | 7536.7691 | 0 | 7456.6005 | 0 | 7700.873
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.43 |  | 0.47 |  | 0.47 |  | 0.46 |  | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.3 |  | 20.1 |  | 20 |  | 19.8 |  | 19.6 |  | 20.8
| LIQUID LEVEL | mm | mm |  | 207.3 |  | 132.9 |  | 202 |  | 214.8 |  | 163 |  | 195.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.7 |  | 5.87 |  | 5.56 |  | 5.73 |  | 5.67 |  | 5.23
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 27
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-27
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK |  | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 71.5 | 69.1 |  | 75.3 |  | 72.6 |  | 70.5 |  | 73.7 | 72.9 | 67.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0.5 |  | 0 |  | 0 |  | 0.1 |  | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% | 66.3 | 63.2 |  | 72.7 |  | 67.2 |  | 67.2 |  | 68.5 | 67.8 | 35.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 66.3 | 65.2 |  | 66.9 |  | 62.6 |  | 64.9 |  | 71.2 | 72.7 | 69.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 35.8 | 33.6 |  | 47.7 |  | 36.5 |  | 28.7 |  | 43.1 | 43.5 | 35.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 119.6 | 115.4 |  | 115.7 |  | 116.7 |  | 114.4 |  | 112.2 | 119.5 | 113.9
| INPUT | Kw | 1194kW | 1170 | 1119 |  | 1157 |  | 1167 |  | 1157 |  | 1180 | 1208 | 1145
COMPRESSOR | RUNNING TIME | Hr | NA | 49663.4 | 49654 |  | 50938 |  | 48590.2 |  | 50961.2 |  | 50144.5 | 50290.3 | 50281
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 59.8 |  | 59.3 |  | 57.7 |  | 57.5 |  | 53.3 | 59.2 | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 |  | 0.49 |  | 0.59 |  | 0.52 |  | 0.47 | 0.5 | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 46.1 |  | 44.8 |  | 45.8 |  | 45 |  | 44.6 | 44.9 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 |  | 0.22 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.4 | 4.2 |  | 3.6 |  | 4.1 |  | 4 |  | 4.1 | 5.1 | 4.5
| SATURATION TEMPERATURE | CELCIUS | C | 3 | 3.6 |  | 2.3 |  | 3.4 |  | 3 |  | 3 | 4 | 3.5
| APPROACH TEMP | CELCIUS | C | 1.8 | 1.2 | 0 | 2.6 | 0 | 1.4 | 0 | 0.9 | 0 | 1.4 | 1.2 | 1.4
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 695.9 | 664.32 |  | 639.36 |  | 637.52 |  | 632.88 |  | 641.68 | 674.3 | 640.08
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.4 | 13.2 |  | 13.3 |  | 13.6 |  | 13.2 |  | 13.3 | 13.2 | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.8 | 4.8 |  | 4.9 |  | 4.8 |  | 3.9 |  | 4.4 | 5.2 | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.6 | 8.4 | 0 | 8.4 | 0 | 8.8 | 0 | 9.3 | 0 | 8.9 | 8 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 6910.7852 | 6443.7506 | 0 | 6201.6443 | 0 | 6478.2633 | 0 | 6796.5173 | 0 | 6594.6328 | 6229.0993 | 6282.5404
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.83 | 0.84 |  | 0.87 |  | 0.86 |  | 0.85 |  | 0.83 | 0.85 | 0.86
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.6 | 36.3 |  | 36.6 |  | 36.6 |  | 36.6 |  | 35.9 | 36.9 | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C | 37 | 37.3 |  | 38.2 |  | 37.9 |  | 37.5 |  | 36.8 | 37.6 | 38
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.2 | 2.9 | 0 | 4.2 | 0 | 3.3 | 0 | 3.3 | 0 | 2.6 | 3.1 | 3.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.1 | 28.7 |  | 28.6 |  | 28.6 |  | 28.4 |  | 28.6 | 28.7 | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.8 | 34.4 |  | 34 |  | 34.6 |  | 34.2 |  | 34.2 | 34.5 | 34.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.7 | 5.7 | 0 | 5.4 | 0 | 6 | 0 | 5.8 | 0 | 5.6 | 5.8 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1220.9 | 1146.88 |  | 1133.02 |  | 1166.06 |  | 1145.34 |  | 1135.82 | 1228.1 | 1145.06
| HEAT CAPACITY | kW | 8226.9 | 8035.9469 | 7548.7483 | 0 | 7065.0208 | 0 | 8078.9376 | 0 | 7670.8684 | 0 | 7344.7945 | 8225.1501 | 7668.9931
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.47 |  | 0.46 |  | 0.46 |  | 0.47 |  | 0.46 | 0.48 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 20.3 | 20 |  | 19.5 |  | 19.9 |  | 19.9 |  | 19.9 | 20.7 | 20.3
| LIQUID LEVEL | mm | mm | 200.4 | 200.8 |  | 124.3 |  | 207.6 |  | 220.1 |  | 158.3 | 199.4 | 201.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.36 | 5.86 |  | 5.4 |  | 5.61 |  | 5.6 |  | 5.51 | 4.97 | 5.14
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 28
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-28
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK |  | OK |  | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 67.8 | 81 | 76.4 |  | 74.7 |  | 73.4 |  | 73.4 | 76.1 | 71.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 60.8 | 76.2 | 71.2 |  | 70.1 |  | 68.8 |  | 67.8 | 70.6 | 65.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69 | 69.5 | 69.7 |  | 64.1 |  | 64.3 |  | 74.7 | 73.3 | 73.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 35.9 | 52.6 | 49 |  | 36.7 |  | 33.4 |  | 52.1 | 45.7 | 40.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 115.8 | 117.7 | 116.2 |  | 119 |  | 116.4 |  | 117.8 | 118.9 | 117.5
| INPUT | Kw | 1194kW |  | 1138 | 1204 | 1176 |  | 1211 |  | 1178 |  | 1187 | 1213 | 1184
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49673.5 | 50955.6 | 50947.8 |  | 48600.3 |  | 50971.4 |  | 50154..7 | 50311.8 | 50323.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 | 59.2 | 59.1 |  | 58 |  | 57.3 |  | 58.7 | 58.8 | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.49 | 0.5 |  | 0.59 |  | 0.52 |  | 0.48 | 0.5 | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 | 44.7 | 44.7 |  | 45 |  | 45.1 |  | 45.1 | 44.8 | 45.2
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.25 | 0.22 | 0.22 |  | 0.21 |  | 0.22 |  | 0.23 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.7 | 3.5 | 3.7 |  | 4.4 |  | 4 |  | 4.4 | 4.7 | 4.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.1 | 2.6 | 2.9 |  | 3.6 |  | 2.9 |  | 3.5 | 3.8 | 3.9
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 2.2 | 2.1 | 0 | 0.9 | 0 | 0.9 | 0 | 0.8 | 0.8 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 653.4 | 628.32 | 638.7 |  | 639.4 |  | 641.2 |  | 633 | 631.12 | 638.5
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.6 | 13.6 | 13.7 |  | 13.4 |  | 12.8 |  | 13 | 13.5 | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 | 4.8 | 5 |  | 4.5 |  | 3.8 |  | 4.3 | 4.6 | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.6 | 8.8 | 8.7 | 0 | 8.9 | 0 | 9 | 0 | 8.7 | 8.9 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6488.7298 | 6384.776 | 6416.5012 | 0 | 6571.2009 | 0 | 6663.7413 | 0 | 6359.2379 | 6486.1062 | 6340.7621
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.85 | 0.85 |  | 0.84 |  | 0.83 |  | 0.83 | 0.83 | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.4 | 36.4 | 37 |  | 36.7 |  | 36.6 |  | 35.7 | 35.7 | 36.7
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.8 | 37.4 | 37.8 |  | 37.4 |  | 37.1 |  | 36.2 | 36.8 | 37.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.1 | 4.2 | 3.7 | 0 | 2.5 | 0 | 2.7 | 0 | 1.7 | 3.5 | 3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.7 | 27.9 | 28.8 |  | 28.9 |  | 28.8 |  | 28.6 | 27.8 | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.7 | 33.2 | 34.1 |  | 34.9 |  | 34.4 |  | 34.5 | 33.3 | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 6 | 5.3 | 5.3 | 0 | 6 | 0 | 5.6 | 0 | 5.9 | 5.5 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1151.9 | 1214.64 | 1131.6 |  | 1162.4 |  | 1148.2 |  | 1141.1 | 1230.32 | 1145.3
| HEAT CAPACITY | kW | 8226.9 | 0 | 7980.8314 | 7433.709 | 6925.4965 | 0 | 8053.5797 | 0 | 7424.8499 | 0 | 7774.2379 | 7813.8106 | 7670.6005
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 | 0.46 | 0.47 |  | 0.47 |  | 0.47 |  | 0.46 | 0.46 | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.5 | 19.3 | 20.2 |  | 19.9 |  | 20 |  | 19.6 | 19.8 | 20.6
| LIQUID LEVEL | mm | mm |  | 193.4 | 129.4 | 123.1 |  | 205.5 |  | 211.7 |  | 151.9 | 194.3 | 204
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.58 | 5.45 | 5.5 |  | 5.48 |  | 5.73 |  | 5.66 | 5.3 | 5.4
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 29
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-29
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 67.7 |  | 75.4 | 76.1 | 73.5 | 73.4 | 74 |  | 73.4 |  | 71.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.8 |  | 0 | 0 | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 61.5 |  | 70.5 | 70.7 | 68.3 | 67.9 | 69.9 |  | 67.8 |  | 64.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.6 |  | 69.8 | 62.8 | 64.2 | 65.8 | 64.9 |  | 74.7 |  | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 35.5 |  | 50.5 | 40 | 36.1 | 33.2 | 30.5 |  | 52.1 |  | 41.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.4 |  | 116.3 | 118.1 | 118.3 | 115.6 | 116.2 |  | 117.8 |  | 116.6
| INPUT | Kw | 1194kW |  | 1128 |  | 1167 | 1196 | 1198 | 1173 | 1182 |  | 1187 |  | 1180
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49682.1 |  | 50966 | 48618.8 | 48609.4 | 50989.8 | 50980.4 |  | 50163.5 |  | 50327.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59.1 | 57.9 | 57.8 | 57.3 | 57.2 |  | 58.7 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 |  | 45 | 45 | 45 | 45 | 45.1 |  | 45.1 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.22 | 0.23 | 0.22 | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.6 | 4.1 | 4.4 | 3.8 | 4 |  | 4.4 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 |  | 2.9 | 3.3 | 3.5 | 3 | 2.9 |  | 3.5 |  | 4
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 0 | 2.1 | 0.8 | 0.7 | 1.1 | 0.9 | 0 | 0.8 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 661.9 |  | 642.3 | 681.2 | 647.21 | 669.2 | 639.1 |  | 643.2 |  | 639.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.6 |  | 13.7 | 12.7 | 13 | 12.7 | 12.8 |  | 13 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.9 |  | 5 | 4.1 | 4.2 | 4.1 | 3.8 |  | 4.3 |  | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.7 | 0 | 8.7 | 8.6 | 8.8 | 8.6 | 9 | 0 | 8.7 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6649.5727 | 0 | 6452.6674 | 6764.8037 | 6576.7298 | 6645.6351 | 6641.9169 | 0 | 6461.709 | 0 | 6277.8291
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 | 0.82 | 0.84 | 0.81 | 0.83 |  | 0.83 |  | 0.85
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.4 |  | 36.9 | 35.9 | 36.8 | 35.8 | 36.6 |  | 35.7 |  | 36.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.9 |  | 37.8 | 36.6 | 37.4 | 36.2 | 37.1 |  | 36.2 |  | 37.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2 | 0 | 3.5 | 2.5 | 2.4 | 2.5 | 2.7 | 0 | 1.7 | 0 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 38.9 |  | 28.9 | 28.6 | 29 | 28.4 | 28.8 |  | 28.6 |  | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.9 |  | 34.3 | 34.1 | 35 | 33.7 | 34.4 |  | 34.5 |  | 34.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | -4 | 0 | 5.4 | 5.5 | 6 | 5.3 | 5.6 | 0 | 5.9 | 0 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1149 |  | 1132.4 | 1299.1 | 1166.4 | 1299.2 | 1147.6 |  | 1140.1 |  | 1156.1
| HEAT CAPACITY | kW | 8226.9 | 0 | -5307.1594 | 0 | 7061.1547 | 8250.6351 | 8081.2933 | 7951.224 | 7420.97 | 0 | 7767.4249 | 0 | 7742.933
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 |  | 0.47 | 0.46 | 0.47 | 0.46 | 0.47 |  | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.4 |  | 20.1 | 19.4 | 20 | 19 | 20 |  | 19.6 |  | 20.7
| LIQUID LEVEL | mm | mm |  | 202.2 |  | 125.1 | 195.9 | 210.5 | 213.7 | 211.7 |  | 151.9 |  | 209.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.69 |  | 5.52 | 5.35 | 5.47 | 5.44 | 5.73 |  | 5.55 |  | 5.36
% OF COOLING CAPACITY | [13 empty] | b
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 30
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-30
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 71.5 | 69.4 |  | 74.2 |  | 73.6 |  | 71.5 | 78.3 | 72.8 |  | 71.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.4 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.1 | 63.3 |  | 69.2 |  | 68.9 |  | 68.1 | 73.4 | 68.1 |  | 64.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 63.9 | 67.6 |  | 70.9 |  | 63.8 |  | 64.9 | 70.3 | 73.6 |  | 72.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 34.8 | 36.9 |  | 47.3 |  | 36.6 |  | 30.2 | 53 | 56.2 |  | 41.1
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118.5 | 117.2 |  | 114.5 |  | 116.4 |  | 115.3 | 120 | 117.1 |  | 117.1
| INPUT | Kw | 1194kW | 1156 | 1161 |  | 1169 |  | 1189 |  | 1175 | 1213 | 1196 |  | 1189
COMPRESSOR | RUNNING TIME | Hr | NA | 49701.2 | 49691.3 |  | 50975.1 |  | 48625.4 |  | 51003.7 | 50183 | 50172.2 |  | 50336.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.6 |  | 59.3 |  | 57.9 |  | 57.3 | 58.5 | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 | 0.47 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 44.9 |  | 44.9 |  | 44.9 |  | 44.8 | 45.1 | 45.1 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.9 | 4.7 |  | 3.9 |  | 4.4 |  | 4 | 3.9 | 4.5 |  | 5.1
| SATURATION TEMPERATURE | CELCIUS | C | 3.5 | 4.1 |  | 3 |  | 3.4 |  | 2.9 | 2.8 | 3.1 |  | 4.1
| APPROACH TEMP | CELCIUS | C | 0.9 | 1.1 | 0 | 2.3 | 0 | 0.8 | 0 | 1.3 | 1.4 | 1.7 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 698.1 | 681 |  | 655.3 |  | 638.5 |  | 635.4 | 684.6 | 660 |  | 648.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.8 | 13.6 |  | 13.6 |  | 13.1 |  | 13 | 12.8 | 13.8 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.4 | 5.2 |  | 5.3 |  | 4.2 |  | 4.2 | 4.2 | 4.8 |  | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.4 | 8.4 | 0 | 8.3 | 0 | 8.9 | 0 | 8.8 | 8.6 | 9 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 6771.4088 | 6605.5427 | 0 | 6280.5889 | 0 | 6561.9515 | 0 | 6456.7206 | 6798.5681 | 6859.1224 | 0 | 6439.0762
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.83 | 0.83 |  | 0.86 |  | 0.84 |  | 0.83 | 0.83 | 0.82 |  | 0.85
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.3 | 36.7 |  | 37.1 |  | 36.8 |  | 36.7 | 35.8 | 36 |  | 37
| SATURATED TEMEPRATURE | CELCIUS | C | 36.9 | 37.1 |  | 38 |  | 37.5 |  | 37.1 | 36.3 | 36.5 |  | 37.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.1 | 2.1 | 0 | 3.7 | 0 | 2.5 | 0 | 2.5 | 1.8 | 1.8 | 0 | 3.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.1 | 28.8 |  | 28.8 |  | 29 |  | 28.8 | 29.2 | 28.7 |  | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.8 | 35 |  | 34.3 |  | 35 |  | 34.6 | 34.5 | 34.7 |  | 34.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.7 | 6.2 | 0 | 5.5 | 0 | 6 | 0 | 5.8 | 5.3 | 6 | 0 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1215.9 | 1155.1 |  | 1140.2 |  | 1165.4 |  | 1148.4 | 1290.6 | 1138.9 |  | 1154
| HEAT CAPACITY | kW | 8226.9 | 8003.037 | 8269.7691 | 0 | 7241.455 | 0 | 8074.3649 | 0 | 7691.3626 | 7898.5912 | 7890.7621 | 0 | 7728.8684
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.48 |  | 0.47 |  | 0.47 |  | 0.47 | 0.45 | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C | 19.8 | 20.6 |  | 20.3 |  | 20.2 |  | 20 | 19.1 | 19.7 |  | 20.8
| LIQUID LEVEL | mm | mm | 201.4 | 196.4 |  | 126.3 |  | 198.6 |  | 218.3 | 154.7 | 156.4 |  | 194.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.33 | 5.4 |  | 5.38 |  | 5.56 |  | 5.52 | 5.24 | 5.56 |  | 5.34
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 31
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-03-31
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 |  | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.9 |  | 76 | 74.9 | 74 | 78.7 | 69.7 |  | 76.5 |  | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 |  | 0 | 0 | 0 | 0.1 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.4 |  | 71.3 | 69.6 | 69.1 | 71.9 | 65.3 |  | 71.6 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.8 |  | 70.6 | 62.6 | 63.8 | 65.9 | 65.2 |  | 74.2 |  | 73.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.3 |  | 52.2 | 42 | 38.2 | 35.2 | 32.1 |  | 53.5 |  | 42
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.5 |  | 115.6 | 119.2 | 116.4 | 118.6 | 112.3 |  | 118.3 |  | 118.5
| INPUT | Kw | 1194kW |  | 1158 |  | 1171 | 1199 | 1182 | 1210 | 1140 |  | 1202 |  | 1205
COMPRESSOR | RUNNING TIME | Hr | NA |  | 49709.5 |  | 50984.8 | 48647.2 | 48636.7 | 51024.5 | 51013.9 |  | 50196.8 |  | 50346.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 59 |  | 58.9 | 58 | 57.8 | 57.3 | 57.2 |  | 58.5 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.47 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 |  | 45.2 | 44.9 | 44.8 | 45 | 45.2 |  | 45.1 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.5 | 4.4 | 4.2 | 4.1 | 3.7 |  | 4.1 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.7 | 3.5 | 3.5 | 3 | 2.7 |  | 3.3 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | 2.1 | 0.8 | 0.7 | 1.6 | 1.1 | 0 | 1.1 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 673 |  | 652.6 | 680.36 | 634.3 | 694.8 | 643.3 |  | 652.8 |  | 643
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.4 |  | 13.6 | 13.1 | 13.4 | 13.1 | 12.8 |  | 13.6 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 |  | 4.8 | 4.3 | 4.2 | 4.6 | 3.8 |  | 4.4 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.6 | 0 | 8.8 | 8.8 | 9.2 | 8.5 | 9 | 0 | 9.2 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6683.3718 | 0 | 6631.5012 | 6913.5889 | 6738.5219 | 6819.6305 | 6685.5658 | 0 | 6935.0577 | 0 | 6385.4503
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.84 | 0.82 | 0.82 | 0.81 | 0.81 |  | 0.82 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 |  | 36.2 | 35.8 | 36 | 35.8 | 35.7 |  | 35.3 |  | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 37.2 | 36.6 | 36.7 | 36.4 | 36.2 |  | 35.7 |  | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.1 | 0 | 3.8 | 2.4 | 2.4 | 2.5 | 2.5 | 0 | 1.6 | 0 | 3.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28 |  | 28.2 | 28.5 | 28.3 | 28.3 | 28.2 |  | 28 |  | 27.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.3 |  | 33.4 | 34.2 | 34.3 | 33.9 | 33.7 |  | 34.1 |  | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 6.3 | 0 | 5.2 | 5.7 | 6 | 5.6 | 5.5 | 0 | 6.1 | 0 | 6
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1155.8 |  | 1149.9 | 1301 | 1177.2 | 1297.9 | 1151.4 |  | 1138.6 |  | 1165.7
| HEAT CAPACITY | kW | 8226.9 | 0 | 8408.2448 | 0 | 6904.7113 | 8563.164 | 8156.1201 | 8392.8868 | 7312.5866 | 0 | 8020.1617 | 0 | 8076.4434
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 |  | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.9 |  | 19.4 | 19.5 | 19.6 | 19.5 | 19.5 |  | 19.1 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 196.9 |  | 120.4 | 206.2 | 205 | 215.3 | 195.4 |  | 159.9 |  | 195.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.6 |  | 5.5 | 5.39 | 5.72 | 5.2 | 5.72 |  | 5.64 |  | 5.26
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO