## 1
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-01
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 71.1 | 70.4 |  | 79.5 |  | 74.1 | 71.5 | 72.1 |  | 77.5 |  | 76.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.6 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 67.3 | 64.5 |  | 76 |  | 69.6 | 66.2 | 66 |  | 73.4 |  | 71.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 66.9 | 69.5 |  | 70.6 |  | 64.4 | 66.1 | 66.4 |  | 75.4 |  | 74
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 39 | 39.4 |  | 55.8 |  | 40.2 | 33 | 32.8 |  | 2.7 |  | 3.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118.7 | 116 |  | 116.5 |  | 116.6 | 113.6 | 113 |  | 119.8 |  | 116
| INPUT | Kw | 1194kW | 1162 | 1141 |  | 1180 |  | 1191 | 1156 | 1142 |  | 1213 |  | 1141
COMPRESSOR | RUNNING TIME | Hr | NA | 50163.6 | 50154.8 |  | 51283.4 |  | 49096.4 | 51477.6 | 51468.8 |  | 50665.1 |  | 50664
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.2 |  | 59.2 |  | 58 | 57.5 | 57.2 |  | 58.7 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.48 |  | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 44.7 |  | 44.8 |  | 44.8 | 45 | 45.1 |  | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.25 | 0.23 |  | 0.21 |  | 0.22 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.2 | 4.2 |  | 3.3 |  | 4.3 | 3.9 | 3.6 |  | 4.5 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 3.7 | 3.6 |  | 2.2 |  | 3.4 | 2.8 | 2.7 |  | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 1 | 1.1 | 0 | 2.7 | 0 | 0.7 | 1 | 1.3 | 0 | 1.4 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 695.3 | 640.8 |  | 649.5 |  | 643.5 | 627.9 | 637.4 |  | 637.5 |  | 634.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.2 | 13.7 |  | 13.6 |  | 13.2 | 13.2 | 13.1 |  | 14.1 |  | 13.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.7 | 4.7 |  | 4.9 |  | 4.1 | 3.8 | 4 |  | 4.7 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.5 | 9 | 0 | 8.7 | 0 | 9.1 | 9.4 | 9.1 | 0 | 9.4 | 0 | 9.1
| CHILLING CAPACITY | kW | 7032.6kW | 6824.5381 | 6659.5843 | 0 | 6525 | 0 | 6761.9515 | 6815.5427 | 6697.8522 | 0 | 6919.746 | 0 | 6666.3279
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.8 |  | 0.82 |  | 0.81 | 0.81 | 0.8 |  | 0.8 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.4 | 35.1 |  | 35.6 |  | 35.4 | 35.6 | 35.1 |  | 34.8 |  | 35.3
| SATURATED TEMEPRATURE | CELCIUS | C | 35.9 | 35.5 |  | 36.4 |  | 36.1 | 36 | 35.6 |  | 35.3 |  | 36.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 1.6 | 1 | 3.1 | 0 | 2.2 | 2.2 | 2.3 | 0 | 1.6 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.7 | 28.3 |  | 28.3 |  | 28.5 | 28.7 | 28.4 |  | 28.1 |  | 28.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.2 | 33.9 |  | 33.3 |  | 33.9 | 33.8 | 33.3 |  | 33.7 |  | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.6 | 0 | 5 | 0 | 5.4 | 5.1 | 4.9 | 0 | 5.6 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1291.2 | 1297.8 |  | 1304 |  | 1294.8 | 1305.9 | 1296.2 |  | 1288.5 |  | 1296.8
| HEAT CAPACITY | kW | 8226.9 | 8200.4619 | 8392.2402 | 0 | 7528.8684 | 0 | 8073.8106 | 7690.6351 | 7334.157 | 0 | 8332.1016 | 0 | 7936.5358
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.46 |  | 0.45 |  | 0.45 | 0.46 | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.5 | 19.4 |  | 18.7 |  | 19.1 | 19.4 | 19.3 |  | 18.9 |  | 19.6
| LIQUID LEVEL | mm | mm | 198.7 | 200.2 |  | 120 |  | 216.9 | 200.8 | 218.9 |  | 163.8 |  | 200.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.59 | 5.84 |  | 5.58 |  | 5.65 | 5.75 | 5.9 |  | 5.78 |  | 5.53
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 2
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-02
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 68.9 |  | 77.3 | 75.5 | 74 |  | 75.8 | 75.8 | 76.1 |  | 72.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.1 |  | 72.1 | 72.7 | 68.8 |  | 70.6 | 70.5 | 70.9 |  | 66.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.4 |  | 68.8 | 63.7 | 63.1 |  | 65.6 | 73.9 | 73.8 |  | 71.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.3 |  | 54.7 | 39.3 | 40 |  | 35.9 | 58.5 | 58.5 |  | 39.3
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.1 |  | 114.7 | 119.1 | 116 |  | 115.2 | 119.3 | 117.2 |  | 114.8
| INPUT | Kw | 1194kW |  | 1149 |  | 1166 | 1207 | 1183 |  | 1180 | 1216 | 1196 |  | 1170
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50175 |  | 51293 | 49116.9 | 49106 |  | 51492 | 50685.7 | 50675 |  | 50674
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.6 |  | 59.1 | 57.7 | 57.6 |  | 44.5 | 58.6 | 45.1 |  | 59
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.52 | 0.48 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  |  | 44 | 45 |  | 45.1 | 44.9 | 45.1 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.29 |  |  | 0.22 | 0.27 |  | 0.23 | 0.23 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 |  |  | 4 | 4 |  | 3.5 | 4.9 | 4 |  | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 2.6 |  |  | 3.2 | 3.2 |  | 2.6 | 3.6 | 2.4 |  | 3.3
| APPROACH TEMP | CELCIUS | C | 0 | 2.1 | 0 | 0 | 0.9 | 1 | 0 | 1.3 | 1.4 | 1.6 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 646.96 |  |  | 640.38 | 639.76 |  | 637.92 | 635.5 | 634.24 |  | 641.92
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  |  | 13.2 | 12.7 |  | 13 | 13.8 | 13 |  | 12.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 |  |  | 4.1 | 4.2 |  | 3.9 | 5 | 4 |  | 4.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.8 | 0 | 0 | 9.1 | 8.5 | 0 | 9.1 | 8.8 | 9 | 0 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6574.1894 | 0 | 0 | 6729.1663 | 6279.3995 | 0 | 6703.3164 | 6457.7367 | 6591.4088 | 0 | 6226.4758
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.3 |  |  | 0.81 | 0.83 |  | 0.82 | 0.82 | 0.8 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 |  |  | 35.2 | 36 |  | 36.1 | 36 | 35.3 |  | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.6 |  |  | 36.2 | 37 |  | 36.3 | 36.4 | 35.8 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2 | 1 | 0 | 2.5 | 3.7 | 0 | 2.9 | 1.5 | 2.3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.5 |  |  | 28.5 | 28.5 |  | 28.4 | 29.5 | 28.5 |  | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.6 |  |  | 33.7 | 33.3 |  | 33.4 | 34.9 | 33.5 |  | 33.8
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 0 | 0 | 5.2 | 4.8 | 0 | 5 | 5.4 | 5 | 0 | 5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1302.98 |  |  | 1291.5 | 1298.36 |  | 1297.38 | 1293.1 | 1293.18 |  | 1293.32
| HEAT CAPACITY | kW | 8226.9 | 0 | 7673.4388 | 0 | 0 | 7754.9654 | 7196.4527 | 0 | 7490.6467 | 8063.2102 | 7466.3972 | 0 | 7467.2055
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  |  | 0.45 | 0.46 |  | 0.46 | 0.46 | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 |  |  | 19.1 | 19.4 |  | 19.4 | 19.9 | 18.9 |  | 19.8
| LIQUID LEVEL | mm | mm |  | 202.7 |  |  | 201.2 | 200.5 |  | 205.9 | 155.5 | 154.2 |  | 200.4
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.69 |  |  | 5.57 | 5.56 |  | 5.87 | 5.33 | 5.63 |  | 5.22
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 3
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-03
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 71 | 71.4 |  | 81.3 |  | 72 | 72.3 | 70.4 | 75.8 | 78.5 |  | 74.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.4 |  | 0 |  | 0 | 0.1 | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 65.5 | 66.3 |  | 77.1 |  | 68.2 | 69.6 | 65 | 70.4 | 74.1 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.5 | 69.5 |  | 70.4 |  | 64.7 | 66.1 | 66.5 | 72.7 | 74.8 |  | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 38 | 42 |  | 56 |  | 42.1 | 34.6 | 34.9 | 52.1 | 58.2 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 115.3 | 115.9 |  | 116.7 |  | 114.6 | 114.2 | 111.9 | 117.6 | 118.9 |  | 116.8
| INPUT | Kw | 1194kW | 1144 | 1125 |  | 1175 |  | 1153 | 1166 | 1133 | 1207 | 1200 |  | 1179
COMPRESSOR | RUNNING TIME | Hr | NA
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.6 | 58 |  | 58.9 |  | 57.7 | 57.2 | 57.2 | 58.7 | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.48 |  | 0.58 | 0.52 | 0.52 | 0.48 | 0.57 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.3 | 45 |  | 45 |  | 45.1 | 45 | 45 | 44.9 | 45 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.21 |  | 0.21 |  | 0.23 | 0.22 | 0.22 | 0.22 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.1 | 3.9 |  | 2.8 |  | 4 | 3.5 | 3.9 | 4.5 | 4 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C | 3.6 | 3.3 |  | 2 |  | 3.2 | 2.5 | 2.4 | 3.2 | 2.8 |  | 3.1
| APPROACH TEMP | CELCIUS | C | 0.9 | 1 | 0 | 2.6 | 0 | 1.4 | 1.3 | 1.3 | 1.4 | 1.3 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 631.2 | 656.4 |  | 635.6 |  | 637.4 | 632.5 | 624.8 | 686.7 | 642.3 |  | 638.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.7 | 13.3 |  | 13.4 |  | 13.5 | 13 | 13 | 13.2 | 13.4 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.5 | 4.3 |  | 4.6 |  | 4.6 | 3.8 | 3.7 | 4.6 | 4.1 |  | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9.2 | 9 | 0 | 8.8 | 0 | 8.9 | 9.2 | 9.3 | 8.6 | 9.3 | 0 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW | 6705.5889 | 6821.709 | 0 | 6458.7529 | 0 | 6550.6467 | 6719.3995 | 6709.746 | 6819.4226 | 6897.679 | 0 | 6566.0624
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.78 |  | 0.8 |  | 0.8 | 0.81 | 0.78 | 0.81 | 0.77 |  | 0.79
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.8 | 34.5 |  | 35 |  | 34.8 | 35.8 | 34.7 | 35.9 | 34.1 |  | 34.7
| SATURATED TEMEPRATURE | CELCIUS | C | 36.2 | 35.1 |  | 36 |  | 35.6 | 36.3 | 35.1 | 36.2 | 34.7 |  | 35.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.6 | 1.7 | 1 | 3.3 | 0 | 2.2 | 2.3 | 2.3 | 1.5 | 1.6 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.1 | 27.9 |  | 27.8 |  | 27.2 | 29 | 27.8 | 29.3 | 27.5 |  | 27.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.6 | 33.4 |  | 32.7 |  | 33.4 | 34 | 32.8 | 34.7 | 33.1 |  | 33
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.5 | 0 | 4.9 | 0 | 6.2 | 5 | 5 | 5.4 | 5.6 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1290.4 | 1295.8 |  | 1300.6 |  | 1295.8 | 1306 | 1293.1 | 1299.6 | 1285.4 |  | 1296.4
| HEAT CAPACITY | kW | 8226.9 | 8195.3811 | 8229.6767 | 0 | 7359.0531 | 0 | 9277.0901 | 7540.4157 | 7465.9353 | 8103.7413 | 8312.0554 | 0 | 8083.7875
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.45 |  | 0.44 |  | 0.45 | 0.45 | 0.45 | 0.46 | 0.44 |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C | 19.7 | 18.9 |  | 18.2 |  | 19 | 19.3 | 19.1 | 19.4 | 18.1 |  | 18.9
| LIQUID LEVEL | mm | mm | 205.4 | 201.7 |  | 117.8 |  | 200.8 | 206 | 206.4 | 157.3 | 160 |  | 199.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 6.08 | 6.04 |  | 5.72 |  | 5.9 | 5.78 | 6 | 5.25 | 5.68 |  | 5.33
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 4
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-04
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 69.4 | 67.9 |  | 78.8 |  | 75.5 |  | 75.3 | 77.1 | 74 |  | 71.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.8 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 66.3 | 61.9 |  | 73.6 |  | 71.2 |  | 69.9 | 71.7 | 68.6 |  | 66.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 66.5 | 68.7 |  | 70.6 |  | 63.5 |  | 65.6 | 73.4 | 75.3 |  | 73.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 38.4 | 35.8 |  | 52.8 |  | 40.2 |  | 35.1 | 56.7 | 53.7 |  | 44.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 116.9 | 116.4 |  | 118.5 |  | 118.8 |  | 117.3 | 118.2 | 118.8 |  | 117.4
| INPUT | Kw | 1194kW | 1144 | 1142 |  | 1190 |  | 1209 |  | 1186 | 1203 | 1196 |  | 1186
COMPRESSOR | RUNNING TIME | Hr | NA | 50210.7 | 50201.5 |  | 51311.8 |  | 49132.3 |  | 51523 | 50717.5 | 50707.9 |  | 50692.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 59.9 |  | 59.2 |  | 57.9 |  | 57.5 | 58.4 | 58.7 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.5 |  | 0.59 |  | 0.52 | 0.48 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 45.9 |  | 45.1 |  | 45 |  | 44.8 | 45 | 44.9 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.22 |  | 0.22 | 0.22 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4 | 4.7 |  | 3.5 |  | 4.1 |  | 3.8 | 4.2 | 4.6 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 3.5 | 4 |  | 2.6 |  | 3.2 |  | 2.4 | 3.3 | 3.5 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 1 | 1 | 0 | 2.3 | 0 | 0.7 | 0 | 1.6 | 1.1 | 1.3 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 688.8 | 666.2 |  | 647.6 |  | 641 |  | 622.6 | 685.8 | 654.1 |  | 638.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.2 | 13.7 |  | 13.8 |  | 13 |  | 13.2 | 13.2 | 13.7 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.5 | 5 |  | 4.9 |  | 3.9 |  | 4 | 4.4 | 4.8 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.7 | 8.7 | 0 | 8.9 | 0 | 9.1 | 0 | 9.2 | 8.8 | 8.9 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 6919.8152 | 6692.7714 | 0 | 6655.4734 | 0 | 6735.6813 | 0 | 6614.2263 | 6968.8684 | 6722.2748 | 0 | 6268.0139
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.82 |  | 0.84 |  | 0.83 |  | 0.81 | 0.8 | 0.8 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.2 | 36 |  | 36.4 |  | 36.3 |  | 36.2 | 34.8 | 35.6 |  | 36.1
| SATURATED TEMEPRATURE | CELCIUS | C | 35.7 | 36.4 |  | 37.3 |  | 37 |  | 36.6 | 35.4 | 36 |  | 36.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 1.5 | 1 | 3.2 | 0 | 2.1 | 0 | 2.1 | 1.7 | 1.5 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.6 | 29.3 |  | 29.4 |  | 29.4 |  | 29.2 | 28.4 | 29.1 |  | 29.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34 | 34.9 |  | 34.1 |  | 34.9 |  | 34.5 | 33.7 | 34.5 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.4 | 5.6 | 0 | 4.7 | 0 | 5.5 | 0 | 5.3 | 5.3 | 5.4 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1290.1 | 1300.7 |  | 1301.7 |  | 1293.5 |  | 1297.5 | 1301.6 | 1293.4 |  | 1298.9
| HEAT CAPACITY | kW | 8226.9 | 8044.5035 | 8410.9931 | 0 | 7064.6536 | 0 | 8215.0693 | 0 | 7940.8199 | 7965.9122 | 8065.0808 | 0 | 7949.388
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.47 |  | 0.46 |  | 0.46 |  | 0.46 | 0.45 | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.4 | 20.2 |  | 19.5 |  | 19.4 |  | 19.5 | 18.7 | 19.3 |  | 20.2
| LIQUID LEVEL | mm | mm | 208 | 200.8 |  | 125.7 |  | 206 |  | 207.3 | 154.1 | 159.4 |  | 193.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.52 | 5.64 |  | 5.38 |  | 5.55 |  | 5.68 | 5.46 | 5.54 |  | 5.27
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 5
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-05
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.4 |  | 79.5 | 75.5 | 74.1 | 72.3 | 72.1 |  | 77.5 |  | 76.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 | 0.1 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.5 |  | 76 | 72.7 | 69.6 | 69.6 | 66 |  | 73.4 |  | 71.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.5 |  | 70.6 | 63.7 | 64.4 | 66.1 | 66.4 |  | 75.4 |  | 74
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 39.4 |  | 55.8 | 39.3 | 40.2 | 34.6 | 32.8 |  | 2.7 |  | 3.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116 |  | 116.5 | 119.1 | 116.6 | 114.2 | 113 |  | 119.8 |  | 116
| INPUT | Kw | 1194kW |  | 1141 |  | 1180 | 1207 | 1191 | 1166 | 1142 |  | 1213 |  | 1141
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50220.3 |  | 51321.9 | 49149.7 | 49142.4 | 51541.3 | 51534 |  | 50729.2 |  | 50702.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.2 | 57.7 | 58 | 57.2 | 57.2 |  | 58.7 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.48 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.7 |  | 44.8 | 44 | 44.8 | 45 | 45.1 |  | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.22 | 0.22 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.2 |  | 3.3 | 4 | 4.3 | 3.5 | 3.6 |  | 4.5 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.6 |  | 2.2 | 3.2 | 3.4 | 2.5 | 2.7 |  | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 0 | 2.1 | 0.9 | 1.1 | 1.3 | 1.2 | 0 | 0.8 | 0 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 642 |  | 631.84 | 640.38 | 630 | 632.5 | 639.12 |  | 635.52 |  | 635.52
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.3 | 13.2 | 13.4 | 13 | 13.1 |  | 13.3 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.5 |  | 4.3 | 4.1 | 4.5 | 3.8 | 3.9 |  | 4.1 |  | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9 | 0 | 9 | 9.1 | 8.9 | 9.2 | 9.2 | 0 | 9.2 | 0 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6672.0554 | 0 | 6566.4665 | 6729.1663 | 6474.5958 | 6719.3995 | 6789.7275 | 0 | 6751.4827 | 0 | 6531.3256
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 |  | 0.83 | 0.81 | 0.82 | 0.81 | 0.81 |  | 0.79 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.1 |  | 35.6 | 35.2 | 35.4 | 35.8 | 35.1 |  | 34.8 |  | 35.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.8 |  | 36.7 | 36.2 | 36.3 | 36.3 | 35.9 |  | 35.4 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.5 | 1 | 3.7 | 2.5 | 2.9 | 2.3 | 3 | 0 | 2.4 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.2 |  | 28 | 28.5 | 28.1 | 29 | 27.9 |  | 28 |  | 28.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.3 |  | 33 | 33.7 | 33.4 | 34 | 32.9 |  | 33 |  | 33.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 0 | 5 | 5.2 | 5.3 | 5 | 5 | 0 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1299.48 |  | 1296.96 | 1291.5 | 1292.34 | 1306 | 1292.06 |  | 1295.98 |  | 1297.8
| HEAT CAPACITY | kW | 8226.9 | 0 | 7652.8268 | 0 | 7488.2217 | 7754.9654 | 7909.2402 | 7540.4157 | 7459.9307 | 0 | 7482.5635 | 0 | 7792.7945
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 | 0.45 | 0.45 | 0.45 | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.4 |  | 18.7 | 19.1 | 19.1 | 19.3 | 19.3 |  | 18.9 |  | 19.6
| LIQUID LEVEL | mm | mm |  | 200.2 |  | 120 | 201.2 | 216.9 | 206 | 218.9 |  | 163.8 |  | 200.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.69 |  | 5.38 | 5.57 | 5.36 | 5.78 | 5.9 |  | 5.87 |  | 5.53
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 6
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-06
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.1 | 71.4 |  | 81.3 |  | 72 | 75.9 | 70.4 |  | 78.5 |  | 74.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.4 |  | 0 |  | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 67.9 | 66.3 |  | 77.1 |  | 68.2 | 73.3 | 65 |  | 74.1 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 68.6 | 69.5 |  | 70.4 |  | 64.7 | 67.5 | 66.5 |  | 74.8 |  | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 43.6 | 42 |  | 56 |  | 42.1 | 36.5 | 34.9 |  | 58.2 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 115.1 | 115.9 |  | 116.7 |  | 114.6 | 116.3 | 111.9 |  | 118.9 |  | 116.8
| INPUT | Kw | 1194kW | 1125 | 1125 |  | 1175 |  | 1153 | 1177 | 1133 |  | 1200 |  | 1179
COMPRESSOR | RUNNING TIME | Hr | NA | 50238.2 | 50230 |  | 51331.8 |  | 49160.1 | 51563.2 | 51555 |  | 50739.1 |  | 50712.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58 |  | 58.9 |  | 57.7 | 57.4 | 57.2 |  | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.48 |  | 0.58 | 0.52 | 0.52 |  | 0.57 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 45 |  | 45 |  | 45.1 | 45.3 | 45 |  | 45 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.21 |  | 0.21 |  | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.5 | 3.9 |  | 2.8 |  | 4 | 3.6 | 3.9 |  | 4 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C | 3 | 3.3 |  | 2 |  | 3.2 | 2.6 | 2.4 |  | 2.8 |  | 3.1
| APPROACH TEMP | CELCIUS | C | 1 | 1.3 | 0 | 2.4 | 0 | 1.3 | 1.3 | 1.6 | 0 | 1.2 | 0 | 1.3
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 624.7 | 646.56 |  | 630.56 |  | 639.52 | 650.1 | 643.68 |  | 633.12 |  | 633.52
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.4 | 13.3 |  | 13.2 |  | 13.5 | 13.1 | 13.5 |  | 13.2 |  | 13.1
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4 | 4.6 |  | 4.4 |  | 4.5 | 3.9 | 4 |  | 4 |  | 4.4
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9.4 | 8.7 | 0 | 8.8 | 0 | 9 | 9.2 | 9.5 | 0 | 9.2 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 6780.8083 | 6495.4642 | 0 | 6407.5381 | 0 | 6646.2818 | 6906.3741 | 7061.1547 | 0 | 6725.9861 | 0 | 6364.4619
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.78 | 0.81 |  | 0.83 |  | 0.82 | 0.79 | 0.82 |  | 0.8 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.4 | 34.5 |  | 35 |  | 34.8 | 34.7 | 34.7 |  | 34.1 |  | 34.7
| SATURATED TEMEPRATURE | CELCIUS | C | 34.9 | 36 |  | 36.9 |  | 36.5 | 35.4 | 36.3 |  | 35.5 |  | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 2.4 | 1 | 3.6 | 0 | 2.9 | 2.3 | 3 | 0 | 2.3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.7 | 28.4 |  | 28.3 |  | 28.3 | 27.7 | 28.1 |  | 28.3 |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.2 | 33.6 |  | 33.3 |  | 33.6 | 33.1 | 33.3 |  | 33.2 |  | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.2 | 0 | 5 | 0 | 5.3 | 5.4 | 5.2 | 0 | 4.9 | 0 | 5
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1306.7 | 1291.5 |  | 1296.82 |  | 1293.6 | 1295.6 | 1293.18 |  | 1299.9 |  | 1295.7
| HEAT CAPACITY | kW | 8226.9 | 8298.903 | 7754.9654 | 0 | 7487.4134 | 0 | 7916.9515 | 8078.7991 | 7765.0531 | 0 | 7355.0924 | 0 | 7480.9469
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.44 | 0.45 |  | 0.44 |  | 0.45 | 0.44 | 0.45 |  | 0.44 |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C | 18.5 | 18.9 |  | 18.2 |  | 19 | 18.7 | 19.1 |  | 18.1 |  | 18.9
| LIQUID LEVEL | mm | mm | 195.6 | 201.7 |  | 117.8 |  | 200.8 | 198.6 | 206.4 |  | 160 |  | 199.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 6.32 | 5.54 |  | 5.72 |  | 5.9 | 5.87 | 5.68 |  | 5.68 |  | 5.33
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 7
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-07
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 68.9 |  | 78.1 | 73.2 | 73.2 |  | 76.7 | 76.7 | 72.8 |  | 74.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 62.5 |  | 74.2 | 69.7 | 68.1 |  | 73.2 | 71.7 | 68.1 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.2 |  | 6.8 | 64.1 | 63.5 |  | 66.4 | 72.8 | 72.2 |  | 69.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 33.5 |  | 46.2 | 40.9 | 36.9 |  | 33.7 | 59.2 | 50.5 |  | 38.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115 |  | 114.2 | 118.5 | 115.3 |  | 117.8 | 119.3 | 116.2 |  | 117.4
| INPUT | Kw | 1194kW |  | 1127 |  | 1169 | 1190 | 1189 |  | 1201 | 1205 | 1186 |  | 1197
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50249.3 |  | 51342.3 | 49179.5 | 49170.6 |  | 51579.7 | 50758.6 | 50749.7 |  | 50722.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59 | 57.8 | 57.5 |  | 57.3 | 58.5 | 58.7 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 | 0.59 | 0.59 |  | 0.52 | 0.47 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 45.1 | 44.9 | 44.9 |  | 45 | 45.1 | 44.7 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.25 |  | 0.21 | 0.23 | 0.23 |  | 0.22 | 0.23 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.1 | 4.6 | 4.4 |  | 3.8 |  | 4.3 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 |  | 2.3 | 3.6 | 3.5 |  | 2.8 | 3.1 | 3.2 |  | 3.4
| APPROACH TEMP | CELCIUS | C |  | 0.3 | 0 | 1.8 | 1.2 | 1 | 0 | 1.1 | 1.2 | 0.7 | 0 | 0.5
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 632 |  | 632 | 678.24 | 634.3 |  | 628 | 686 | 635.6 |  | 636.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.8 |  | 12.5 | 13.3 | 12.8 |  | 13.5 | 12.7 | 12.4 |  | 12.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.3 |  | 4.1 | 4.8 | 4.5 |  | 3.9 | 4.3 | 3.9 |  | 3.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.5 | 0 | 8.4 | 8.5 | 8.3 | 0 | 9.6 | 8.4 | 8.5 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6203.2333 | 0 | 6130.254 | 6657.0901 | 6079.3187 | 0 | 6961.6628 | 6654.0416 | 6238.5681 | 0 | 6246.4203
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.84 |  | 0.86 | 0.83 | 0.85 |  | 0.81 | 0.8 | 0.88 |  | 0.85
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.6 |  | 37.1 | 36 | 37 |  | 37 | 35.1 | 36.4 |  | 37
| SATURATED TEMEPRATURE | CELCIUS | C |  | 37.2 |  | 38 | 36.8 | 37.7 |  | 37.5 | 35.6 | 36.8 |  | 37.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.6 | 1 | 3.1 | 2.8 | 2.1 | 0 | 2.2 | 2.3 | 1.4 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 30.3 |  | 30.3 | 28.5 | 30.2 |  | 30.1 | 28.2 | 30 |  | 30.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 35.6 |  | 34.9 | 34 | 35.6 |  | 35.3 | 33.3 | 35.4 |  | 35.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 0 | 4.6 | 5.5 | 5.4 | 0 | 5.2 | 5.1 | 5.4 | 0 | 5.1
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1284.3 |  | 1284.9 | 1292.06 | 1299.6 |  | 1270.6 | 1296.12 | 1251.1 |  | 1298.9
| HEAT CAPACITY | kW | 8226.9 | 0 | 7860.0346 | 0 | 6825.1039 | 8205.9238 | 8103.7413 | 0 | 7629.4688 | 7633.0393 | 7801.3164 | 0 | 7649.4111
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 |  | 0.46 | 0.46 | 0.47 |  | 0.47 | 0.48 | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.6 |  | 19.8 | 19.7 | 20.2 |  | 19.9 | 19.6 | 19.9 |  | 20.3
| LIQUID LEVEL | mm | mm |  | 199.8 |  | 128.4 | 206.9 | 204.8 |  | 203.9 | 165 | 162.3 |  | 200
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.85 |  | 5.56 | 5.4 | 5.57 |  | 5.62 | 5.31 | 5.57 |  | 5.34
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 8
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-08
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.6 |  | 78.5 |  | 73.4 |  | 72 |  | 73.7 |  | 73.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.4 |  | 0 |  | 0 |  | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.6 |  | 73.3 |  | 58.1 |  | 68.7 |  | 71 |  | 68.4
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.2 |  | 71.7 |  | 64.4 |  | 68 |  | 739 |  | 72.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.6 |  | 51.7 |  | 38.6 |  | 32.4 |  | 53.8 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117 |  | 115.9 |  | 117.6 |  | 115.6 |  | 118 |  | 118.8
| INPUT | Kw | 1194kW |  | 1138 |  | 1180 |  | 1192 |  | 1171 |  | 1197 |  | 1197
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50257.6 |  | 51350.9 |  | 49187 |  | 51588.1 |  | 50772.6 |  | 50730.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59 |  | 60.3 |  | 57.3 |  | 58.7 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.2 |  | 45.1 |  | 46.6 |  | 45 |  | 44.8 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.3 |  | 4.4 |  | 4 |  | 4.5 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 |  | 2.6 |  | 3.5 |  | 3.1 |  | 3.5 |  | 3.7
| APPROACH TEMP | CELCIUS | C |  | 0.8 | 0 | 2.3 | 0 | 0.7 | 0 | 1.2 | 0 | 1.1 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 657.2 |  | 634.9 |  | 635.97 |  | 622.2 |  | 639.2 |  | 637.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.9 |  | 13.8 |  | 13.3 |  | 13.8 |  | 13.9 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 |  | 4.9 |  | 4.2 |  | 4.3 |  | 4.6 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.2 | 0 | 8.9 | 0 | 9.1 | 0 | 9.5 | 0 | 9.3 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6981.8014 | 0 | 6524.9538 | 0 | 6682.8256 | 0 | 6825.5196 | 0 | 6864.388 | 0 | 6479.0762
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.84 |  | 0.83 |  | 0.82 |  | 0.8 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.8 |  | 36.3 |  | 36.2 |  | 36.1 |  | 35.5 |  | 36
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 37.2 |  | 36.9 |  | 36.6 |  | 35.9 |  | 36.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.7 | 1 | 3.2 | 0 | 2.1 | 0 | 1.8 | 0 | 1.6 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.3 |  | 29.2 |  | 29.3 |  | 29.3 |  | 29 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.7 |  | 34 |  | 34.8 |  | 34.8 |  | 34.3 |  | 34.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.4 | 0 | 4.8 | 0 | 5.5 | 0 | 5.5 | 0 | 5.3 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1296.3 |  | 1298.2 |  | 1293.1 |  | 1296.7 |  | 1294.8 |  | 1298.3
| HEAT CAPACITY | kW | 8226.9 | 0 | 8083.164 | 0 | 7195.5658 | 0 | 8212.5289 | 0 | 8235.3926 | 0 | 7924.2956 | 0 | 7945.7159
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 |  | 0.46 |  | 0.46 |  | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.9 |  | 19.5 |  | 19.7 |  | 19.7 |  | 19.2 |  | 20
| LIQUID LEVEL | mm | mm |  | 198.8 |  | 122.9 |  | 214.5 |  | 209.4 |  | 160.4 |  | 195.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.97 |  | 5.62 |  | 5.64 |  | 6 |  | 5.73 |  | 5.34
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 9
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-09
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 68.2 |  | 77.3 | 74.5 | 74 |  | 73.9 | 78.2 | 74.5 |  | 73.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 61.8 |  | 72.7 | 69.2 | 68 |  | 70.2 | 74 | 69.7 |  | 68.4
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.8 |  | 70.9 | 64.1 | 64.6 |  | 68.3 | 74.4 | 75.2 |  | 73.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36 |  | 51.3 | 38.2 | 38.9 |  | 34.1 | 54.7 | 53.3 |  | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.9 |  | 117.1 | 117.8 | 117.9 |  | 117.9 | 120.5 | 118.5 |  | 119.2
| INPUT | Kw | 1194kW |  | 1130 |  | 1175 | 1195 | 1186 |  | 1191 | 1221 | 1191 |  | 1201
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50277.3 |  | 51360.5 | 49204.8 | 49195.7 |  | 51612.1 | 50791.3 | 50782.2 |  | 50739.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.2 | 57.6 | 57.5 |  | 57.6 | 44.9 | 58.8 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.52 | 0.47 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 44.9 | 45.2 | 45 |  | 44.8 | 44.9 | 44.9 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.5 |  | 3.4 | 4 | 4.1 |  | 4.2 | 4.2 | 4.4 |  | 4.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 |  | 2.5 | 3.2 | 3.3 |  | 3.1 | 3 | 3.2 |  | 3.9
| APPROACH TEMP | CELCIUS | C |  | 0.8 | 0 | 2.5 | 1.4 | 0.7 | 0 | 1.3 | 1.3 | 1.3 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 638.1 |  | 626.3 | 639.2 | 648.9 |  | 638.4 | 636.9 | 637.7 |  | 631.8
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.9 |  | 13.9 | 13.5 | 13 |  | 13.5 | 13.5 | 13.5 |  | 13.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 |  | 5 | 4.6 | 4 |  | 4.4 | 4.3 | 4.5 |  | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.1 | 0 | 8.9 | 8.9 | 9 | 0 | 9.1 | 9.2 | 9 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6705.2079 | 0 | 6436.5704 | 6569.1455 | 6743.7644 | 0 | 6708.3603 | 6766.1432 | 6627.3672 | 0 | 6347.1824
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 |  | 0.84 | 0.83 | 0.83 |  | 0.81 | 0.8 | 0.8 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.9 |  | 36.3 | 36.2 | 36.2 |  | 36.2 | 35.4 | 35.6 |  | 36.1
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.3 |  | 37.2 | 36.9 | 36.9 |  | 36.7 | 35.8 | 35.9 |  | 36.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.6 | 0 | 3.1 | 2.1 | 2.1 | 0 | 2.2 | 1.4 | 1.5 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.3 |  | 29.2 | 29.4 | 29.4 |  | 29.2 | 28.8 | 29 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.7 |  | 34.1 | 34.8 | 34.8 |  | 34.5 | 34.4 | 34.4 |  | 34.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.4 | 0 | 4.9 | 5.4 | 5.4 | 0 | 5.3 | 5.6 | 5.4 | 0 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1303.5 |  | 1293.8 | 1290.1 | 1302.9 |  | 1298.5 | 1299.4 | 1293.6 |  | 1297.7
| HEAT CAPACITY | kW | 8226.9 | 0 | 8128.06 | 0 | 7320.5774 | 8044.5035 | 8124.3187 | 0 | 7946.94 | 8402.5866 | 8066.3279 | 0 | 8241.7436
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.46 | 0.46 |  | 0.46 | 0.45 | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 |  | 19.3 | 19.4 | 19.6 |  | 19.8 | 19.6 | 19.2 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 200.7 |  | 120.1 | 206.4 | 202.2 |  | 203.2 | 164.8 | 158.7 |  | 200.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 6.06 |  | 5.53 | 5.61 | 5.6 |  | 5.6 | 5.63 | 5.65 |  | 5.35
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 10
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-10
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 71.1 | 70.4 |  | 79.5 |  | 74.1 | 71.5 | 72.1 |  | 77.5 |  | 76.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.6 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 67.3 | 64.5 |  | 76 |  | 69.6 | 66.2 | 66 |  | 73.4 |  | 71.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 66.9 | 69.5 |  | 70.6 |  | 64.4 | 66.1 | 66.4 |  | 75.4 |  | 74
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 39 | 39.4 |  | 55.8 |  | 40.2 | 33 | 32.8 |  | 2.7 |  | 3.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118.7 | 116 |  | 116.5 |  | 116.6 | 113.6 | 113 |  | 119.8 |  | 116
| INPUT | Kw | 1194kW | 1162 | 1141 |  | 1180 |  | 1191 | 1156 | 1142 |  | 1213 |  | 1141
COMPRESSOR | RUNNING TIME | Hr | NA | 50287 | 50278.1 |  | 51369.8 |  | 49216.3 | 51631 | 51622 |  | 50806 |  | 50748
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.2 |  | 59.2 |  | 58 | 57.5 | 57.2 |  | 58.7 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.48 |  | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 44.7 |  | 44.8 |  | 44.8 | 45 | 45.1 |  | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.25 | 0.23 |  | 0.21 |  | 0.22 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.2 | 4.2 |  | 3.3 |  | 4.3 | 3.9 | 3.6 |  | 4.5 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 3.7 | 3.6 |  | 2.2 |  | 3.4 | 2.8 | 2.7 |  | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 1 | 1.1 | 0 | 2.7 | 0 | 0.7 | 1 | 1.3 | 0 | 1.4 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 695.3 | 640.8 |  | 649.5 |  | 643.5 | 627.9 | 637.4 |  | 637.5 |  | 634.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.2 | 13.7 |  | 13.6 |  | 13.2 | 13.2 | 13.1 |  | 14.1 |  | 13.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.7 | 4.7 |  | 4.9 |  | 4.1 | 3.8 | 4 |  | 4.7 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.5 | 9 | 0 | 8.7 | 0 | 9.1 | 9.4 | 9.1 | 0 | 9.4 | 0 | 9.1
| CHILLING CAPACITY | kW | 7032.6kW | 6824.5381 | 6659.5843 | 0 | 6525 | 0 | 6761.9515 | 6815.5427 | 6697.8522 | 0 | 6919.746 | 0 | 6666.3279
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.8 |  | 0.82 |  | 0.81 | 0.81 | 0.8 |  | 0.8 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.4 | 35.1 |  | 35.6 |  | 35.4 | 35.6 | 35.1 |  | 34.8 |  | 35.3
| SATURATED TEMEPRATURE | CELCIUS | C | 35.9 | 35.5 |  | 36.4 |  | 36.1 | 36 | 35.6 |  | 35.3 |  | 36.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 1.6 | 1 | 3.1 | 0 | 2.2 | 2.2 | 2.3 | 0 | 1.6 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.7 | 28.3 |  | 28.3 |  | 28.5 | 28.7 | 28.4 |  | 28.1 |  | 28.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.2 | 33.9 |  | 33.3 |  | 33.9 | 33.8 | 33.3 |  | 33.7 |  | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.6 | 0 | 5 | 0 | 5.4 | 5.1 | 4.9 | 0 | 5.6 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1291.2 | 1297.8 |  | 1304 |  | 1294.8 | 1305.9 | 1296.2 |  | 1288.5 |  | 1296.8
| HEAT CAPACITY | kW | 8226.9 | 8200.4619 | 8392.2402 | 0 | 7528.8684 | 0 | 8073.8106 | 7690.6351 | 7334.157 | 0 | 8332.1016 | 0 | 7936.5358
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.46 |  | 0.45 |  | 0.45 | 0.46 | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.5 | 19.4 |  | 18.7 |  | 19.1 | 19.4 | 19.3 |  | 18.9 |  | 19.6
| LIQUID LEVEL | mm | mm | 198.7 | 200.2 |  | 120 |  | 216.9 | 200.8 | 218.9 |  | 163.8 |  | 200.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.59 | 5.84 |  | 5.58 |  | 5.65 | 5.75 | 5.9 |  | 5.78 |  | 5.53
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 11
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-11
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.1 | 71.4 |  | 81.3 |  | 72 | 75.9 | 70.4 |  | 78.5 |  | 74.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.4 |  | 0 |  | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 67.9 | 66.3 |  | 77.1 |  | 68.2 | 73.3 | 65 |  | 74.1 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 68.6 | 69.5 |  | 70.4 |  | 64.7 | 67.5 | 66.5 |  | 74.8 |  | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 43.6 | 42 |  | 56 |  | 42.1 | 36.5 | 34.9 |  | 58.2 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 115.1 | 115.9 |  | 116.7 |  | 114.6 | 116.3 | 111.9 |  | 118.9 |  | 116.8
| INPUT | Kw | 1194kW | 1125 | 1125 |  | 1175 |  | 1153 | 1177 | 1133 |  | 1200 |  | 1179
COMPRESSOR | RUNNING TIME | Hr | NA
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58 |  | 58.9 |  | 57.7 | 57.4 | 57.2 |  | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.48 |  | 0.58 | 0.52 | 0.52 |  | 0.57 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 45 |  | 45 |  | 45.1 | 45.3 | 45 |  | 45 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.21 |  | 0.21 |  | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.5 | 3.9 |  | 2.8 |  | 4 | 3.6 | 3.9 |  | 4 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C | 3 | 3.3 |  | 2 |  | 3.2 | 2.6 | 2.4 |  | 2.8 |  | 3.1
| APPROACH TEMP | CELCIUS | C | 1 | 1.3 | 0 | 2.4 | 0 | 1.3 | 1.3 | 1.6 | 0 | 1.2 | 0 | 1.3
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 624.7 | 646.56 |  | 630.56 |  | 639.52 | 650.1 | 643.68 |  | 633.12 |  | 633.52
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.4 | 13.3 |  | 13.2 |  | 13.5 | 13.1 | 13.5 |  | 13.2 |  | 13.1
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4 | 4.6 |  | 4.4 |  | 4.5 | 3.9 | 4 |  | 4 |  | 4.4
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9.4 | 8.7 | 0 | 8.8 | 0 | 9 | 9.2 | 9.5 | 0 | 9.2 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 6780.8083 | 6495.4642 | 0 | 6407.5381 | 0 | 6646.2818 | 6906.3741 | 7061.1547 | 0 | 6725.9861 | 0 | 6364.4619
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.78 | 0.81 |  | 0.83 |  | 0.82 | 0.79 | 0.82 |  | 0.8 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.4 | 34.5 |  | 35 |  | 34.8 | 34.7 | 34.7 |  | 34.1 |  | 34.7
| SATURATED TEMEPRATURE | CELCIUS | C | 34.9 | 36 |  | 36.9 |  | 36.5 | 35.4 | 36.3 |  | 35.5 |  | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 2.4 | 1 | 3.6 | 0 | 2.9 | 2.3 | 3 | 0 | 2.3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.7 | 28.4 |  | 28.3 |  | 28.3 | 27.7 | 28.1 |  | 28.3 |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.2 | 33.6 |  | 33.3 |  | 33.6 | 33.1 | 33.3 |  | 33.2 |  | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.2 | 0 | 5 | 0 | 5.3 | 5.4 | 5.2 | 0 | 4.9 | 0 | 5
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1306.7 | 1291.5 |  | 1296.82 |  | 1293.6 | 1295.6 | 1293.18 |  | 1299.9 |  | 1295.7
| HEAT CAPACITY | kW | 8226.9 | 8298.903 | 7754.9654 | 0 | 7487.4134 | 0 | 7916.9515 | 8078.7991 | 7765.0531 | 0 | 7355.0924 | 0 | 7480.9469
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.44 | 0.45 |  | 0.44 |  | 0.45 | 0.44 | 0.45 |  | 0.44 |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C | 18.5 | 18.9 |  | 18.2 |  | 19 | 18.7 | 19.1 |  | 18.1 |  | 18.9
| LIQUID LEVEL | mm | mm | 195.6 | 201.7 |  | 117.8 |  | 200.8 | 198.6 | 206.4 |  | 160 |  | 199.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 6.32 | 5.54 |  | 5.72 |  | 5.9 | 5.87 | 5.68 |  | 5.68 |  | 5.33
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 12
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-12
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 75 | 69.9 |  | 78.4 |  | 74 | 78.5 | 73.9 |  | 76.7 |  | 74.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.8 | 0.6 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 70.1 | 64.3 |  | 74.2 |  | 70 | 73.9 | 69.1 |  | 71.9 |  | 70.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 67.3 | 69.2 |  | 69.7 |  | 64.2 | 67.6 | 68.7 |  | 74.7 |  | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 40 | 37.9 |  | 54.1 |  | 38.5 | 37.8 | 34.6 |  | 56.5 |  | 45.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 119.9 | 115.2 |  | 115.8 |  | 116.4 | 121.1 | 115 |  | 117.5 |  | 117.6
| INPUT | Kw | 1194kW | 1172 | 1124 |  | 1175 |  | 1178 | 1230 | 1172 |  | 1196 |  | 1199
COMPRESSOR | RUNNING TIME | Hr | NA | 50316.4 | 50306.8 |  | 51389.9 |  | 49246.2 | 51663.7 | 51654.1 |  | 50833.3 |  | 50775.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 59.9 |  | 59.2 |  | 57.9 | 57.3 | 57.5 |  | 58.7 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.5 |  | 0.59 | 0.59 | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.2 | 45.9 |  | 45.1 |  | 45 | 44.2 | 44.8 |  | 44.9 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.25 | 0.23 |  | 0.22 |  | 0.22 | 0.23 | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4 | 4.7 |  | 3.5 |  | 4.1 | 4.4 | 3.8 |  | 4.6 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 3.5 | 4 |  | 2.6 |  | 3.2 | 2.5 | 2.4 |  | 3.5 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 1 | 1 | 0 | 2.3 | 0 | 0.7 | 2 | 1.6 | 0 | 1.3 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 690.32 | 667.8 |  | 649.2 |  | 640.7 | 699.76 | 643.4 |  | 656.3 |  | 647.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.9 | 13.7 |  | 13.8 |  | 13 | 13.3 | 13.2 |  | 13.7 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.5 | 5 |  | 4.9 |  | 3.9 | 4.5 | 4 |  | 4.8 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.4 | 8.7 | 0 | 8.9 | 0 | 9.1 | 8.8 | 9.2 | 0 | 8.9 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 6695.9446 | 6708.8453 | 0 | 6671.9169 | 0 | 6732.5289 | 7110.7252 | 6835.1963 | 0 | 6744.8845 | 0 | 6354.388
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.82 |  | 0.84 |  | 0.83 | 0.83 | 0.81 |  | 0.8 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.7 | 36 |  | 36.4 |  | 36.3 | 36.1 | 36.2 |  | 35.6 |  | 36.1
| SATURATED TEMEPRATURE | CELCIUS | C | 36.2 | 36.4 |  | 37.3 |  | 37 | 36.6 | 36.6 |  | 36 |  | 36.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.5 | 1.5 | 1 | 3.2 | 0 | 2.1 | 3 | 2.1 | 0 | 1.5 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.4 | 29.3 |  | 29.4 |  | 29.4 | 28.2 | 29.2 |  | 29.1 |  | 29.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.7 | 34.9 |  | 34.1 |  | 34.9 | 33.6 | 34.5 |  | 34.5 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.3 | 5.6 | 0 | 4.7 | 0 | 5.5 | 5.4 | 5.3 | 0 | 5.4 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1295.14 | 1299.3 |  | 1294.5 |  | 1295.9 | 1291.08 | 1293.8 |  | 1287.1 |  | 1295.6
| HEAT CAPACITY | kW | 8226.9 | 7926.3764 | 8401.94 | 0 | 7025.5774 | 0 | 8230.3118 | 8050.6143 | 7918.1755 | 0 | 8025.7968 | 0 | 7929.1917
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.47 |  | 0.46 |  | 0.46 | 0.46 | 0.46 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.5 | 20.2 |  | 19.5 |  | 19.4 | 19.7 | 19.5 |  | 19.3 |  | 20.2
| LIQUID LEVEL | mm | mm | 198.7 | 200.8 |  | 125.7 |  | 206 | 215.2 | 207.3 |  | 159.4 |  | 193.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.62 | 5.64 |  | 5.38 |  | 5.55 | 5.12 | 5.68 |  | 5.54 |  | 5.27
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 13
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-13
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OIK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.5 |  | 76 | 76.1 | 72.6 |  | 74.4 | 74.4 | 75.8 |  | 71.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65 |  | 71.1 | 70.9 | 68 |  | 58.3 | 71.7 | 71.7 |  | 65.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.5 |  | 70.4 | 64.3 | 63.6 |  | 68.5 | 72.9 | 74.7 |  | 74.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 36.8 |  | 53.3 | 37.4 | 37.9 |  | 32.9 | 51.5 | 51.2 |  | 40.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 118.2 |  | 117.6 | 117.7 | 115.8 |  | 116.4 | 118 | 120.1 |  | 117.4
| INPUT | Kw | 1194kW |  | 1140 |  | 1178 | 1205 | 1174 |  | 1178 | 1208 | 1211 |  | 1183
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50324.9 |  | 51398.2 | 49266.5 | 49255.4 |  | 51675 | 50853.9 | 50842.8 |  | 50784.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59.3 | 57.9 | 58.4 |  | 57.7 | 58.5 | 58.6 |  | 61.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.59 | 0.58 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 45 | 45.1 | 45.3 |  | 45.5 | 45.1 | 45.1 |  | 47.3
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.24 |  | 0.22 | 0.23 | 0.23 |  | 0.23 | 0.22 | 0.23 |  | 0.24
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.8 | 4 | 4.3 |  | 4.1 | 4.4 | 4.5 |  | 5
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 |  | 2.9 | 3.1 | 3.5 |  | 3.2 | 3.7 | 3.3 |  | 4.1
| APPROACH TEMP | CELCIUS | C | 0 | 0.6 | 0 | 2 | 1.5 | 1.2 | 0 | 1.1 | 1.3 | 1 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 642.8 |  | 630 | 636 | 628.64 |  | 637.36 | 684.8 | 621.12 |  | 656.32
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.6 | 13.7 | 13.6 |  | 13.6 | 13.6 | 13.6 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.9 | 4.6 | 4.7 |  | 4.3 | 5 | 4.3 |  | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.9 | 0 | 8.7 | 9.1 | 8.9 | 0 | 9.3 | 8.6 | 9.3 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6606.1432 | 0 | 6329.0993 | 6683.1409 | 6460.6189 | 0 | 6844.6282 | 6800.5543 | 6670.2263 | 0 | 6441.94
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 | 0.84 | 0.84 |  | 0.83 | 0.82 | 0.82 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 |  | 36.4 | 36.6 | 36.3 |  | 36.4 | 35.7 | 35.8 |  | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.7 |  | 37.5 | 37.2 | 37.2 |  | 36.9 | 36.2 | 36.2 |  | 37.1
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.5 | 1 | 3.6 | 2 | 2.8 | 0 | 2.9 | 1.6 | 2.2 | 0 | 2.7
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.1 |  | 29 | 29.7 | 29 |  | 28.8 | 29.3 | 28.9 |  | 29.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.2 |  | 33.9 | 35.2 | 34.4 |  | 34 | 34.6 | 34 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 0 | 4.9 | 5.5 | 5.4 | 0 | 5.2 | 5.3 | 5.1 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1291.5 |  | 1303.26 | 1310.2 | 1292.48 |  | 1300.32 | 1288.7 | 1288.42 |  | 1301.02
| HEAT CAPACITY | kW | 8226.9 | 0 | 7605.8314 | 0 | 7374.1039 | 8321.1316 | 8059.3441 | 0 | 7807.9261 | 7886.963 | 7587.6928 | 0 | 7962.3626
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.46 | 0.46 |  | 0.46 | 0.46 | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 |  | 19.8 | 19.5 | 19.8 |  | 19.8 | 19.4 | 19.5 |  | 20.4
| LIQUID LEVEL | mm | mm |  | 204.4 |  | 118.4 | 206.6 | 195 |  | 195.1 | 152.2 | 151.1 |  | 223.4
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 6.12 |  | 5.43 | 5.67 | 5.67 |  | 5.76 | 5.36 | 5.75 |  | 5.17
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 14
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-14
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 75.3 | 70.4 |  | 79.5 |  | 74.1 | 77.2 | 72.1 |  | 77.5 |  | 76.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.6 |  | 0 |  | 0 | 0.1 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 70.8 | 64.5 |  | 76 |  | 69.6 | 74.5 | 66 |  | 73.4 |  | 71.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 66.7 | 69.5 |  | 70.6 |  | 64.4 | 67.6 | 66.4 |  | 75.4 |  | 74
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 40 | 39.4 |  | 55.8 |  | 40.2 | 35.8 | 32.8 |  | 2.7 |  | 3.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 119.4 | 116 |  | 116.5 |  | 116.6 | 118.8 | 113 |  | 119.8 |  | 116
| INPUT | Kw | 1194kW | 1175 | 1141 |  | 1180 |  | 1191 | 1213 | 1142 |  | 1213 |  | 1141
COMPRESSOR | RUNNING TIME | Hr | NA | 50345.2 | 50335.1 |  | 51408.7 |  | 49275.8 | 51695.6 | 51685.6 |  | 50865.6 |  | 50795
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.2 |  | 59.2 |  | 58 | 57.3 | 57.2 |  | 58.7 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.48 |  | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 44.7 |  | 44.8 |  | 44.8 | 45 | 45.1 |  | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.21 |  | 0.22 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.1 | 4.2 |  | 3.3 |  | 4.3 | 4.1 | 3.6 |  | 4.5 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 3.6 | 3.6 |  | 2.2 |  | 3.4 | 3.4 | 2.7 |  | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 1 | 0.9 | 0 | 2.7 | 0 | 1.1 | 1.1 | 1.5 | 0 | 1 | 0 | 0.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 697.6 | 628.32 |  | 639.84 |  | 628.48 | 675.4 | 627.28 |  | 629.52 |  | 606.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.5 | 13.3 |  | 13.5 |  | 13.5 | 13.5 | 13.6 |  | 13.3 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.6 | 4.5 |  | 4.9 |  | 4.5 | 4.5 | 4.2 |  | 4.3 |  | 4.4
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.9 | 8.8 | 0 | 8.6 | 0 | 9 | 9 | 9.4 | 0 | 9 | 0 | 9.1
| CHILLING CAPACITY | kW | 7032.6kW | 7169.3303 | 6384.776 | 0 | 6354.0693 | 0 | 6531.5473 | 7019.1686 | 6808.8129 | 0 | 6542.3557 | 0 | 6372.1016
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.82 |  | 0.84 |  | 0.83 | 0.82 | 0.83 |  | 0.81 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.6 | 35.1 |  | 35.6 |  | 35.4 | 35.8 | 35.1 |  | 34.8 |  | 35.3
| SATURATED TEMEPRATURE | CELCIUS | C | 36.1 | 36.2 |  | 37.3 |  | 36.9 | 36.5 | 36.8 |  | 36 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 2.3 | 1 | 3.7 | 0 | 2.9 | 2.4 | 3 | 0 | 2.3 | 0 | 2.6
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.9 | 28.7 |  | 28.7 |  | 28.7 | 28.8 | 28.5 |  | 28.7 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.4 | 33.9 |  | 33.6 |  | 34 | 34.1 | 33.8 |  | 33.7 |  | 34
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.2 | 0 | 4.9 | 0 | 5.3 | 5.3 | 5.3 | 0 | 5 | 0 | 5
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1296.5 | 1294.44 |  | 1299.76 |  | 1296.68 | 1302.2 | 1291.08 |  | 1292.76 |  | 1297.1
| HEAT CAPACITY | kW | 8226.9 | 8234.1224 | 7772.6189 | 0 | 7354.3002 | 0 | 7935.8014 | 7969.5843 | 7901.5289 | 0 | 7463.9723 | 0 | 7489.03
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.46 |  | 0.45 |  | 0.45 | 0.46 | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.3 | 19.4 |  | 18.7 |  | 19.1 | 19.4 | 19.3 |  | 18.9 |  | 19.6
| LIQUID LEVEL | mm | mm | 202.9 | 200.2 |  | 120 |  | 216.9 | 208.9 | 218.9 |  | 163.8 |  | 200.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.6 | 5.84 |  | 5.58 |  | 5.65 | 5.48 | 5.9 |  | 5.78 |  | 5.53
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 15
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-15
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 68 |  | 77.5 | 74 | 72.9 |  | 75.8 | 76.6 | 73.6 |  | 73.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 61.3 |  | 73.3 | 71.8 | 68.2 |  | 73 | 72.1 | 68.1 |  | 67.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.2 |  | 71.3 | 63.1 | 63.9 |  | 67 | 73.9 | 74.8 |  | 727
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 35.8 |  | 49.9 | 37.2 | 36.5 |  | 33 | 58.3 | 81 |  | 41.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.6 |  | 123.2 | 118.2 | 117 |  | 118.5 | 118.5 | 118.2 |  | 117.4
| INPUT | Kw | 1194kW |  | 1141 |  | 1191 | 1209 | 1190 |  | 1200 | 1212 | 1196 |  | 1186
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50355 |  | 51417.5 | 49295.1 | 49284.5 |  | 51708.8 | 50884.8 | 50874.2 |  | 50803.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 60.5 |  | 59.8 | 57.9 | 59.1 |  | 57.6 | 58.7 | 59.2 |  | 60.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.52 | 0.46 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 47.2 |  | 45.1 | 44.9 | 45.2 |  | 45 | 44.9 | 44.9 |  | 46
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.21 |  | 0.22 | 0.23 | 0.23 |  | 0.22 | 0.23 | 0.28 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 5 |  | 3.7 | 4.2 | 4.6 |  | 3.9 | 4.3 | 4.6 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.4 |  | 2.9 | 3.3 | 3.6 |  | 3.7 | 3.3 | 3.7 |  | 3.4
| APPROACH TEMP | CELCIUS | C | 0 | 0.6 | 0 | 2.1 | 1.1 | 1 | 0 | 0.6 | 1.1 | 0.9 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 375.2 |  | 647.2 | 630.56 | 632.7 |  | 639.6 | 637.84 | 639 |  | 594.8
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.5 | 13.4 | 13.6 |  | 13.7 | 13.5 | 13.5 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 |  | 5 | 4.4 | 4.6 |  | 4.3 | 4.4 | 4.6 |  | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.5 | 0 | 8.5 | 9 | 9 | 0 | 9.4 | 9.1 | 8.9 | 0 | 9.1
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 3682.679 | 0 | 6352.4249 | 6553.164 | 6575.4042 | 0 | 6942.5404 | 6702.4758 | 6567.0901 | 0 | 6250.2079
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 | 0.84 | 0.84 |  | 0.84 | 0.81 | 0.62 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.5 |  | 36.9 | 36.6 | 36.7 |  | 36.8 | 35.7 | 36.1 |  | 36.6
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.9 |  | 37.8 | 37.2 | 37.4 |  | 37.2 | 36.2 | 36.4 |  | 37.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.7 | 1 | 3.3 | 2.8 | 2.1 | 0 | 2.2 | 2.3 | 1.5 | 0 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.9 |  | 29.8 | 29 | 29.9 |  | 29.8 | 28.8 | 29.6 |  | 29.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 35.2 |  | 34.5 | 34.4 | 35.3 |  | 35 | 33.9 | 34.9 |  | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 0 | 4.7 | 5.4 | 5.4 | 0 | 5.2 | 5.1 | 5.3 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1293.8 |  | 1300.3 | 1290.8 | 1295.7 |  | 1298 | 1294.02 | 1294.3 |  | 1293.3
| HEAT CAPACITY | kW | 8226.9 | 0 | 7918.1755 | 0 | 7057.0554 | 8048.8684 | 8079.4226 | 0 | 7793.9954 | 7620.6721 | 7921.2356 | 0 | 7915.1155
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 |  | 0.47 | 0.46 | 0.47 |  | 0.46 | 0.46 | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.6 |  | 20 | 19.6 | 20 |  | 19.8 | 19.9 | 19.9 |  | 20.2
| LIQUID LEVEL | mm | mm |  | 188.6 |  | 123.2 | 204.1 | 204.2 |  | 198.5 | 165.2 | 159.9 |  | 206.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.63 |  | 5.53 | 5.63 | 5.58 |  | 5.58 | 5.64 | 5.6 |  | 5.5
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 16
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-16
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.4 | 69.4 |  | 80.7 |  | 73.4 | 74.5 | 74.5 |  | 74.4 |  | 74
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.1 |  | 0 |  | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.5 | 63.6 |  | 76.7 |  | 67.5 | 70 | 70 |  | 72.2 |  | 69.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 68.5 | 69.6 |  | 70.4 |  | 63.3 | 67.5 | 67.7 |  | 72.4 |  | 72.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 36.9 | 35.4 |  | 48.2 |  | 36.4 | 33.1 | 32.4 |  | 56.1 |  | 38.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 117.5 | 116 |  | 118 |  | 115 | 117.7 | 116 |  | 117.8 |  | 117.5
| INPUT | Kw | 1194kW | 1161 | 1140 |  | 1203 |  | 1176 | 1189 | 1188 |  | 1207 |  | 1197
COMPRESSOR | RUNNING TIME | Hr | NA | 50374.3 | 50365.6 |  | 51428.4 |  | 49303.4 | 51728.4 | 51719.7 |  | 50899.4 |  | 50814.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 58.1 |  | 59.5 |  | 57.7 | 57.4 | 57.4 |  | 58.7 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.59 | 0.52 | 0.52 |  | 0.47 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.2 | 45 |  | 44.8 |  | 45 | 44.8 | 45.1 |  | 45.1 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.21 |  | 0.22 | 0.22 | 0.22 |  | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4 | 4.3 |  | 3.3 |  | 4 | 4.1 | 3.8 |  | 4.2 |  | 4.4
| SATURATION TEMPERATURE | CELCIUS | C | 3.6 | 4 |  | 2.4 |  | 3.3 | 3.6 | 3.7 |  | 3.1 |  | 3.4
| APPROACH TEMP | CELCIUS | C | 0.7 | 0.7 | 0 | 2.6 |  | 0.7 | 0.5 | 0.4 | 0 | 1.1 | 0 | 1.5
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 628.64 | 632.4 |  | 633.1 |  | 636.63 | 640.08 | 639.6 |  | 641.8 |  | 607.3
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.5 | 14 |  | 13.9 |  | 12.9 | 13.5 | 13.3 |  | 13.4 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 4.7 |  | 5 |  | 4 | 4.1 | 4.1 |  | 4.2 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9.2 | 9.3 | 0 | 8.9 | 0 | 8.9 | 9.4 | 9.2 | 0 | 9.2 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 6678.3926 | 6791.3626 | 0 | 6506.455 | 0 | 6542.7333 | 6947.7506 | 6794.8268 | 0 | 6818.1986 | 0 | 5960.7968
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.83 |  | 0.85 |  | 0.84 | 0.83 | 0.81 |  | 0.62 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.1 | 36.5 |  | 37.1 |  | 36.8 | 36.3 | 36.7 |  | 36.2 |  | 36.7
| SATURATED TEMEPRATURE | CELCIUS | C | 36.6 | 37 |  | 37.9 |  | 37.4 | 36.9 | 37.2 |  | 36.4 |  | 37.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 2.4 | 1.7 | 1 | 3.2 | 0 | 2 | 2.9 | 2.2 | 0 | 1.4 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.9 | 30 |  | 29.9 |  | 30 | 28.7 | 29.9 |  | 29.7 |  | 29.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.2 | 35.3 |  | 34.7 |  | 35.4 | 34 | 35 |  | 35 |  | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.3 | 5.3 | 0 | 4.8 | 0 | 5.4 | 5.3 | 5.1 | 0 | 5.3 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1307.6 | 1295.9 |  | 1300.2 |  | 1297.7 | 1287.02 | 1298 |  | 1292.5 |  | 1298.9
| HEAT CAPACITY | kW | 8226.9 | 8002.6328 | 7931.0277 | 0 | 7206.6513 | 0 | 8091.8938 | 7876.6813 | 7644.1109 | 0 | 7910.2194 | 0 | 7799.3995
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.48 |  | 0.46 |  | 0.47 | 0.47 | 0.47 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.7 | 20.4 |  | 19.7 |  | 20.1 | 19.8 | 20 |  | 19.4 |  | 20.2
| LIQUID LEVEL | mm | mm | 199.2 | 200.9 |  | 120.6 |  | 204.4 | 213.6 | 211.2 |  | 161.3 |  | 203.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 6.03 | 6.03 |  | 5.47 |  | 5.59 | 5.68 | 5.71 |  | 5.62 |  | 5.57
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 17
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-17
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 71.8 | 73.4 | 82.8 | 77.3 |  | 73.3 |  | 74.4 |  | 74.3 |  | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.1 | 0 | 0 |  | 0 |  | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.7 | 68.5 | 79.1 | 72.3 |  | 67.1 |  | 70 |  | 69.1 |  | 69.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 66.8 | 68.8 | 69.2 | 70.9 |  | 65.4 |  | 67.9 |  | 75 |  | 72.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 39 | 39 | 52.1 | 53.5 |  | 37.1 |  | 35.7 |  | 54.6 |  | 45.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118.3 | 119.6 | 118.1 | 117.6 |  | 116.4 |  | 117 |  | 117.4 |  | 119.4
| INPUT | Kw | 1194kW | 1153 | 1160 | 1195 | 1180 |  | 1166 |  | 1178 |  | 1183 |  | 1201
COMPRESSOR | RUNNING TIME | Hr | NA | 50398.3 | 50388.5 | 51446.7 | 51436.9 |  | 49311.8 |  | 51742.6 |  | 50908 |  | 50822.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.4 | 58.8 | 59.1 | 59.3 |  | 58.1 |  | 57.3 |  | 58.7 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 | 0.48 | 0.49 |  | 0.58 |  | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.8 | 45 | 45.1 | 45.1 |  | 45 |  | 45.1 |  | 45.1 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.25 | 0.23 | 0.21 | 0.22 |  | 0.22 |  | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.1 | 4 | 2.9 | 3.6 |  | 3.9 |  | 3.8 |  | 4.1 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 3.8 | 3.7 | 2.1 | 2.8 |  | 3.2 |  | 2.8 |  | 3.3 |  | 3.5
| APPROACH TEMP | CELCIUS | C | 0.8 | 0.9 | 2.7 | 2.1 |  | 0.8 | 0 | 1.3 | 0 | 1 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 697.2 | 635.7 | 678.1 | 639.2 |  | 639.9 |  | 628.8 |  | 634.5 |  | 630.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.1 | 14.1 | 13.2 | 14.1 |  | 13 |  | 13.4 |  | 13.6 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.6 | 4.6 | 4.8 | 4.9 |  | 4 |  | 4.1 |  | 4.3 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.5 | 9.5 | 8.4 | 9.2 | 0 | 9 | 0 | 9.3 | 0 | 9.3 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 6843.1871 | 6973.6143 | 6577.4134 | 6790.5774 | 0 | 6650.2309 | 0 | 6752.7021 | 0 | 6813.9145 | 0 | 6338.1409
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.88 | 0.81 | 0.83 | 0.83 |  | 0.82 |  | 0.82 |  | 0.82 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.4 | 35.8 | 35.9 | 36.1 |  | 35.9 |  | 35.9 |  | 35.2 |  | 35.9
| SATURATED TEMEPRATURE | CELCIUS | C | 36 | 36.2 | 36.8 | 37 |  | 36.6 |  | 36.4 |  | 35.6 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 1.7 | 1 | 3.2 | 0 | 2.1 | 0 | 2.3 | 0 | 1.6 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.7 | 29.1 | 28.7 | 29 |  | 29.1 |  | 29 |  | 28.8 |  | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.3 | 34.5 | 33.6 | 33.8 |  | 34.5 |  | 34.1 |  | 34 |  | 34.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 5.4 | 4.9 | 4.8 | 0 | 5.4 | 0 | 5.1 | 0 | 5.2 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1278 | 1292.3 | 1278 | 1293.6 |  | 1296.1 |  | 1297.6 |  | 1297.2 |  | 1291.3
| HEAT CAPACITY | kW | 8226.9 | 8264.2032 | 8058.2217 | 7231.1778 | 7170.0693 | 0 | 8081.9169 | 0 | 7641.7552 | 0 | 7789.1917 | 0 | 8051.9861
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.46 | 0.45 | 0.46 |  | 0.46 |  | 0.46 |  | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.4 | 19.6 | 18.8 | 19.5 |  | 19.7 |  | 19.5 |  | 19 |  | 19.8
| LIQUID LEVEL | mm | mm | 197.6 | 198.2 | 127.4 | 124.7 |  | 204 |  | 207.5 |  | 159 |  | 195.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.56 | 6.09 | 5.37 | 5.58 |  | 5.73 |  | 5.83 |  | 5.78 |  | 5.48
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 18
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-18
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.4 |  | 79.5 | 73.9 | 74.1 | 76.8 | 72.1 |  | 77.5 |  | 76.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.5 |  | 76 | 70.5 | 69.6 | 72.7 | 66 |  | 73.4 |  | 71.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.5 |  | 70.6 | 63.3 | 64.4 | 67.3 | 66.4 |  | 75.4 |  | 74
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 39.4 |  | 55.8 | 38.8 | 40.2 | 34.6 | 32.8 |  | 2.7 |  | 3.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116 |  | 116.5 | 117.6 | 116.6 | 119.4 | 113 |  | 119.8 |  | 116
| INPUT | Kw | 1194kW |  | 1141 |  | 1180 | 1191 | 1191 | 1210 | 1142 |  | 1213 |  | 1141
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50409 |  | 51461 | 49332.2 | 49322 | 51763.3 | 51752 |  | 50918 |  | 50833
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.2 | 57.5 | 58 | 57.5 | 57.2 |  | 58.7 |  | 58.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.48 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.7 |  | 44.8 | 45.4 | 44.8 | 45 | 45.1 |  | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.23 | 0.22 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.2 |  | 3.3 | 4.2 | 4.3 | 4.2 | 3.6 |  | 4.5 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.6 |  | 2.2 | 3.4 | 3.4 | 3 | 2.7 |  | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 0 | 2.1 | 0.6 | 1.1 | 1.3 | 1.2 | 0 | 0.8 | 0 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 642 |  | 631.84 | 641.42 | 630 | 639.8 | 639.12 |  | 635.52 |  | 635.52
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.3 | 13.1 | 13.4 | 13.5 | 13.1 |  | 13.3 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.5 |  | 4.3 | 4 | 4.5 | 4.3 | 3.9 |  | 4.1 |  | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9 | 0 | 9 | 9.1 | 8.9 | 9.2 | 9.2 | 0 | 9.2 | 0 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6672.0554 | 0 | 6566.4665 | 6740.0947 | 6474.5958 | 6796.9515 | 6789.7275 | 0 | 6751.4827 | 0 | 6531.3256
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 |  | 0.83 | 0.84 | 0.82 | 0.81 | 0.81 |  | 0.79 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.1 |  | 35.6 | 36.6 | 35.4 | 36.8 | 35.1 |  | 34.8 |  | 35.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.8 |  | 36.7 | 37.4 | 36.3 | 37.3 | 35.9 |  | 35.4 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.5 | 1 | 3.7 | 2.2 | 2.9 | 2.3 | 3 | 0 | 2.4 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.2 |  | 28 | 29.9 | 28.1 | 29.7 | 27.9 |  | 28 |  | 28.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.3 |  | 33 | 35.2 | 33.4 | 35 | 32.9 |  | 33 |  | 33.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 0 | 5 | 5.3 | 5.3 | 5.3 | 5 | 0 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1299.48 |  | 1296.96 | 1298.6 | 1292.34 | 1291.7 | 1292.06 |  | 1295.98 |  | 1297.8
| HEAT CAPACITY | kW | 8226.9 | 0 | 7652.8268 | 0 | 7488.2217 | 7947.552 | 7909.2402 | 7905.3233 | 7459.9307 | 0 | 7482.5635 | 0 | 7792.7945
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 | 0.47 | 0.45 | 0.47 | 0.46 |  | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.4 |  | 18.7 | 19.8 | 19.1 | 20.1 | 19.3 |  | 18.9 |  | 19.6
| LIQUID LEVEL | mm | mm |  | 200.2 |  | 120 | 198.7 | 216.9 | 205.2 | 218.9 |  | 163.8 |  | 200.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.69 |  | 5.38 | 5.67 | 5.36 | 5.62 | 5.9 |  | 5.87 |  | 5.53
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 19
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-19
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 74 | 70.6 |  | 78.5 |  | 73.4 |  | 72 | 76.8 | 73.7 |  | 73.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.8 | 0.4 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.5 | 64.6 |  | 73.3 |  | 58.1 |  | 68.7 | 71.7 | 71 |  | 68.4
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.4 | 69.2 |  | 71.7 |  | 64.4 |  | 68 | 75 | 739 |  | 72.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 39.8 | 36.6 |  | 51.7 |  | 38.6 |  | 32.4 | 53.7 | 53.8 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 120 | 117 |  | 115.9 |  | 117.6 |  | 115.6 | 119.6 | 118 |  | 118.8
| INPUT | Kw | 1194kW | 1170 | 1138 |  | 1180 |  | 1192 |  | 1171 | 1216 | 1197 |  | 1197
COMPRESSOR | RUNNING TIME | Hr | NA | 50428.2 | 50497.6 |  | 51471 |  | 49335 |  | 51769.2 | 50937.7 | 50925 |  | 50839
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.1 |  | 59 |  | 60.3 |  | 57.3 | 58.7 | 58.7 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 | 0.48 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 45.2 |  | 45.1 |  | 46.6 |  | 45 | 44.9 | 44.8 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 | 0.23 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.4 | 4.3 |  | 3.3 |  | 4.4 |  | 4 | 4.6 | 4.5 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C | 4 | 3.9 |  | 2.6 |  | 3.5 |  | 3.1 | 3.5 | 3.5 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 1 | 0.8 | 0 | 2.3 | 0 | 0.7 | 0 | 1.2 | 1.3 | 1.1 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 689.9 | 657.2 |  | 634.9 |  | 635.97 |  | 622.2 | 663.8 | 639.2 |  | 637.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.9 | 13.9 |  | 13.8 |  | 13.3 |  | 13.8 | 13.8 | 13.9 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5 | 4.7 |  | 4.9 |  | 4.2 |  | 4.3 | 4.8 | 4.6 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.9 | 9.2 | 0 | 8.9 | 0 | 9.1 | 0 | 9.5 | 9 | 9.3 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 7090.1963 | 6981.8014 | 0 | 6524.9538 | 0 | 6682.8256 | 0 | 6825.5196 | 6898.6143 | 6864.388 | 0 | 6479.0762
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.82 |  | 0.84 |  | 0.83 |  | 0.82 | 0.81 | 0.8 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36 | 35.8 |  | 36.3 |  | 36.2 |  | 36.1 | 35.7 | 35.5 |  | 36
| SATURATED TEMEPRATURE | CELCIUS | C | 36.6 | 36.4 |  | 37.2 |  | 36.9 |  | 36.6 | 36.1 | 35.9 |  | 36.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 1.7 | 1 | 3.2 | 0 | 2.1 | 0 | 1.8 | 1.5 | 1.6 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.3 | 29.3 |  | 29.2 |  | 29.3 |  | 29.3 | 29.1 | 29 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.9 | 34.7 |  | 34 |  | 34.8 |  | 34.8 | 34.6 | 34.3 |  | 34.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 5.4 | 0 | 4.8 | 0 | 5.5 | 0 | 5.5 | 5.5 | 5.3 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1297.3 | 1296.3 |  | 1298.2 |  | 1293.1 |  | 1296.7 | 1297.4 | 1294.8 |  | 1298.3
| HEAT CAPACITY | kW | 8226.9 | 8389.0069 | 8083.164 | 0 | 7195.5658 | 0 | 8212.5289 | 0 | 8235.3926 | 8239.8383 | 7924.2956 | 0 | 7945.7159
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.47 |  | 0.46 |  | 0.46 |  | 0.46 | 0.46 | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.9 | 19.9 |  | 19.5 |  | 19.7 |  | 19.7 | 19.4 | 19.2 |  | 20
| LIQUID LEVEL | mm | mm | 199.3 | 198.8 |  | 122.9 |  | 214.5 |  | 209.4 | 159.7 | 160.4 |  | 195.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.6 | 5.97 |  | 5.62 |  | 5.64 |  | 5.9 | 5.47 | 5.73 |  | 5.34
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 20
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-20
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.8 |  | 81 | 75.2 | 74.1 | 75.4 | 76.4 |  | 76.8 |  | 74
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 |  | 0 | 0 | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.6 |  | 76.2 | 71 | 68.5 | 70.9 | 70.9 |  | 71.7 |  | 69.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.3 |  | 70.7 | 64.1 | 63.8 | 67.3 | 68.2 |  | 74.7 |  | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 41.3 |  | 52.6 | 39.3 | 37.6 | 38.1 | 37.4 |  | 55.4 |  | 44.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.6 |  | 117.8 | 116.1 | 117 | 118.8 | 117.8 |  | 119.4 |  | 118.3
| INPUT | Kw | 1194kW |  | 1136 |  | 1191 | 1191 | 1187 | 1211 | 1185 |  | 1200 |  | 1190
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50436.8 |  | 51479 | 49359.6 | 49349.3 | 51796.3 | 51786.1 |  | 50951.4 |  | 50851.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 59.9 |  | 59.2 | 57.8 | 57.9 | 57.5 | 57.5 |  | 58.7 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 | 0.59 | 0.59 | 0.53 | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.9 |  | 45.1 | 45.1 | 45 | 44.8 | 44.8 |  | 44.9 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.23 | 0.22 | 0.23 | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.3 | 4.1 | 4.2 | 4.6 | 3.7 |  | 4.3 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.4 | 3.2 | 3.3 | 3.6 | 2.8 |  | 3.2 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | 2.3 | 0.7 | 0.7 | 1.3 | 1.3 | 0 | 1.4 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 668.6 |  | 643.9 | 628.9 | 640.5 | 708.7 | 625.7 |  | 648.6 |  | 629.2
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.9 |  | 13.9 | 13.1 | 13.1 | 13.3 | 13.5 |  | 13.8 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 |  | 4.7 | 3.9 | 4 | 4.9 | 4.1 |  | 4.6 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.1 | 0 | 9.2 | 9.2 | 9.1 | 8.4 | 9.4 | 0 | 9.2 | 0 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 7025.7044 | 0 | 6840.5081 | 6681.1547 | 6730.4273 | 6874.2263 | 6791.6628 | 0 | 6890.4388 | 0 | 6466.3741
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.84 | 0.83 | 0.83 | 0.83 | 0.81 |  | 0.8 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.4 |  | 36 | 36.1 | 35.7 | 36.3 | 35.6 |  | 35 |  | 35.7
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.9 |  | 36.9 | 36.9 | 36.4 |  | 36.2 |  | 35.6 |  | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.7 | 1 | 3.4 | 2.2 | 2.2 | -34.6 | 2.3 | 0 | 1.7 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.8 |  | 28.9 | 29.3 | 28.8 | 29.1 | 28.7 |  | 28.5 |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.2 |  | 33.5 | 34.7 | 34.2 | 34.6 | 33.9 |  | 33.9 |  | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.4 | 0 | 4.6 | 5.4 | 5.4 | 5.5 | 5.2 | 0 | 5.4 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1302.2 |  | 1296.3 | 1283.9 | 1298.6 | 1295.1 | 1293.6 |  | 1292.9 |  | 1290.9
| HEAT CAPACITY | kW | 8226.9 | 0 | 8119.9538 | 0 | 6885.6582 | 8005.843 | 8097.5058 | 8225.2309 | 7767.5751 | 0 | 8061.963 | 0 | 7900.4273
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.46 | 0.46 | 0.47 | 0.46 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 |  | 19.5 | 19.5 | 19.4 | 20.2 | 19.5 |  | 19.3 |  | 20.2
| LIQUID LEVEL | mm | mm |  | 200.4 |  | 125.6 | 200.1 | 204 | 203.3 | 207.2 |  | 160 |  | 193.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.87 |  | 5.67 | 5.71 | 5.65 | 5.12 | 5.83 |  | 5.75 |  | 5.56
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 21
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-21
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 74.6 |  | 80.7 | 74.3 | 74.6 |  | 74 | 76.8 | 78 |  | 73.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 68.7 |  | 76.3 | 69.5 | 69.5 |  | 71.5 | 72.3 | 74 |  | 67.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.8 |  | 70.2 | 63.7 | 64 |  | 68 | 74 | 75.3 |  | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 38.6 |  | 53.3 | 35.7 | 38.8 |  | 34.3 | 54.6 | 56.8 |  | 45
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 119.4 |  | 118.3 | 117 | 117.2 |  | 117.9 | 121 | 119.9 |  | 117.5
| INPUT | Kw | 1194kW |  | 1172 |  | 1197 | 1187 | 1193 |  | 1193 | 1232 | 1215 |  | 1189
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50446.4 |  | 51488.6 | 49379.9 | 49367.6 |  | 51807.5 | 50973.4 | 50961.1 |  | 50861.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 |  | 59.4 | 57.5 | 57.7 |  | 57.2 | 58.6 | 58.6 |  | 59.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 | 0.59 | 0.58 |  | 0.52 | 0.48 | 0.49 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 44.8 | 45 | 44.9 |  | 45 | 45 | 44.6 |  | 45.4
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.23 | 0.23 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.3 | 4.1 | 4 |  | 3.9 | 4.7 | 4.2 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.6 |  | 2.3 | 3.1 | 3.4 |  | 3.1 | 3.8 | 3.1 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 0 | 2.3 | 1 | 1.2 | 0 | 1 | 1.2 | 1 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 662.24 |  | 640 | 631.9 | 638.4 |  | 639.84 | 689.9 | 643.68 |  | 636.16
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.3 |  | 13.3 | 13.2 | 13.6 |  | 13.5 | 13.8 | 13.3 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.5 |  | 4.6 | 4.1 | 4.6 |  | 4.1 | 5 | 4.1 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.8 | 0 | 8.7 | 9.1 | 9 | 0 | 9.4 | 8.8 | 9.2 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6729.4596 | 0 | 6429.5612 | 6640.0577 | 6634.642 | 0 | 6945.1455 | 7010.5312 | 6838.1709 | 0 | 6464.4434
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 |  | 0.83 | 0.84 | 0.82 |  | 0.81 | 0.82 | 0.8 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.6 |  | 36.9 | 37 | 35.7 |  | 35.6 | 36.3 | 35 |  | 35.6
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.9 |  | 36.8 | 37.7 | 36.4 |  | 36.2 | 36.8 | 35.5 |  | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.4 | 1 | 3.8 | 2.1 | 2.9 | 0 | 3.2 | 1.6 | 2.5 | 0 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.3 |  | 28 | 30.2 | 28.1 |  | 27.9 | 29.8 | 27.9 |  | 28.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.5 |  | 33 | 35.6 | 33.5 |  | 33 | 35.2 | 33 |  | 33.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 0 | 5 | 5.4 | 5.4 | 0 | 5.1 | 5.4 | 5.1 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1298.78 |  | 1296.54 | 1294.3 | 1296.26 |  | 1296.12 | 1298.3 | 1295.84 |  | 1294.86
| HEAT CAPACITY | kW | 8226.9 | 0 | 7798.679 | 0 | 7485.7968 | 8070.6928 | 8082.9145 | 0 | 7633.0393 | 8095.6351 | 7631.3903 | 0 | 7775.1409
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 | 0.47 | 0.46 |  | 0.46 | 0.46 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.5 |  | 19 | 20.1 | 19.1 |  | 19.8 | 19.8 | 18.7 |  | 19.8
| LIQUID LEVEL | mm | mm |  | 197.3 |  | 118.5 | 207.1 | 210.2 |  | 203.5 | 162.6 | 154.5 |  | 200.4
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.71 |  | 5.4 | 5.65 | 5.64 |  | 5.83 | 5.31 | 5.78 |  | 5.3
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 22
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-22
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.4 | 74.6 |  | 80.7 |  | 74.6 |  | 74 | 77.8 | 78 |  | 73.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.8 | 0.1 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 67.6 | 68.7 |  | 76.3 |  | 69.5 |  | 71.5 | 74 | 74 |  | 67.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 68.2 | 69.8 |  | 70.2 |  | 64 |  | 68 | 74 | 75.3 |  | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 38.2 | 38.6 |  | 53.3 |  | 38.8 |  | 34.3 | 50.1 | 56.8 |  | 45
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 119.8 | 119.4 |  | 118.3 |  | 117.2 |  | 117.9 | 121.2 | 119.9 |  | 117.5
| INPUT | Kw | 1194kW | 1181 | 1172 |  | 1197 |  | 1193 |  | 1193 | 1241 | 1215 |  | 1189
COMPRESSOR | RUNNING TIME | Hr | NA | 50466.8 | 50457.1 |  | 51499.1 |  | 49390.3 |  | 51818.2 | 50990.4 | 50980.8 |  | 50871.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.4 | 58.4 |  | 59.4 |  | 57.7 |  | 57.2 | 58.7 | 58.6 |  | 59.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 |  | 0.49 |  | 0.58 |  | 0.52 | 0.48 | 0.49 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 44.8 |  | 44.8 |  | 44.9 |  | 45 | 44.9 | 44.6 |  | 45.4
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.23 |  | 0.23 | 0.23 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.6 | 4.3 |  | 3.3 |  | 4 |  | 3.9 | 4.7 | 4.2 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 4.1 | 3.6 |  | 2.3 |  | 3.4 |  | 3.1 | 3.5 | 3.1 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 1.1 | 1.2 | 0 | 2.5 | 0 | 1.3 | 0 | 0.8 | 1.5 | 1.5 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 701.1 | 633.84 |  | 639.44 |  | 635.28 |  | 635.92 | 688.6 | 628.4 |  | 640.96
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.7 | 13.6 |  | 13.4 |  | 13.6 |  | 13.2 | 13.8 | 13.6 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5.2 | 4.8 |  | 4.8 |  | 4.7 |  | 3.9 | 5 | 4.6 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.5 | 8.8 | 0 | 8.6 | 0 | 8.9 | 0 | 9.3 | 8.8 | 9 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 6881.4665 | 6440.8684 | 0 | 6350.097 | 0 | 6528.8591 | 0 | 6829.164 | 6997.321 | 6530.7159 | 0 | 6365.1917
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.83 | 0.83 |  | 0.85 |  | 0.84 |  | 0.84 | 0.82 | 0.82 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.5 | 35.6 |  | 36.9 |  | 35.7 |  | 35.6 | 36.2 | 35 |  | 35.6
| SATURATED TEMEPRATURE | CELCIUS | C | 37 | 36.9 |  | 37.7 |  | 37.4 |  | 37.1 | 36.7 | 36.4 |  | 37.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 2.4 | 1 | 3.6 | 0 | 2.9 | 0 | 2.9 | 1.6 | 2.3 | 0 | 2.7
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.7 | 29.4 |  | 29.2 |  | 29.2 |  | 29.1 | 29.6 | 29.2 |  | 29.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 35.3 | 34.5 |  | 34.1 |  | 34.5 |  | 34.2 | 35.1 | 34.1 |  | 34.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 5.1 | 0 | 4.9 | 0 | 5.3 | 0 | 5.1 | 5.5 | 4.9 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1298.8 | 1294.58 |  | 1297.38 |  | 1299.2 |  | 1291.78 | 1293 | 1296.96 |  | 1296.26
| HEAT CAPACITY | kW | 8226.9 | 8398.7067 | 7623.97 | 0 | 7340.8337 | 0 | 7951.224 | 0 | 7607.4804 | 8211.8938 | 7338.4573 | 0 | 7783.5473
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.46 |  | 0.45 |  | 0.46 |  | 0.46 | 0.46 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 20.3 | 19.5 |  | 19 |  | 19.1 |  | 19.8 | 19.7 | 18.7 |  | 19.8
| LIQUID LEVEL | mm | mm | 211.4 | 197.3 |  | 118.5 |  | 210.2 |  | 203.5 | 162.1 | 154.5 |  | 200.4
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.36 | 5.71 |  | 5.4 |  | 5.64 |  | 5.83 | 5.31 | 5.78 |  | 5.3
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 23
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-23
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 68.6 |  | 78.6 | 74.2 | 75.2 | 75 | 75 |  | 76.4 |  | 73.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.4 |  | 0 | 0 | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 61.5 |  | 73.3 | 70.7 | 70.7 | 69.6 | 69.6 |  | 74 |  | 67.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.9 |  | 70.2 | 63.9 | 64.1 | 67.8 | 66.9 |  | 74 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 35.6 |  | 50.9 | 37.4 | 39.5 | 34.7 | 35.6 |  | 53.6 |  | 43.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 114.4 |  | 116.6 | 117.9 | 116.9 | 117.8 | 116.3 |  | 119.7 |  | 117.4
| INPUT | Kw | 1194kW |  | 1119 |  | 1182 | 1197 | 1194 | 1187 | 1186 |  | 1219 |  | 1194
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50477.4 |  | 51508.5 | 49408.5 | 49399.7 | 51836.4 | 51827.6 |  | 51004.5 |  | 50880.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59.2 | 57.9 | 57.9 | 57.3 | 57.2 |  | 58.7 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53. |  | 0.49 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 45 | 45.3 | 45.1 | 45.4 | 45.1 |  | 44.5 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.25 |  | 0.22 | 0.23 | 0.22 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.4 | 4.3 | 4.2 | 4 | 3.9 |  | 4.3 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 |  | 2.5 | 3.3 | 3.3 | 3 | 3.4 |  | 3.3 |  | 3.6
| APPROACH TEMP | CELCIUS | C |  | 0.7 | 0 | 2.3 | 1.2 | 1.2 | 0.9 | 0.5 | 0 | 1.1 | 0 | 1.3
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 635.4 |  | 627.4 | 643.04 | 636 | 650.64 | 626 |  | 633.3 |  | 630.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 |  | 13.6 | 13.3 | 13.5 | 13.2 | 13.3 |  | 13.6 |  | 13.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.8 | 4.5 | 4.5 | 3.9 | 3.9 |  | 4.4 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.9 | 0 | 8.8 | 8.8 | 9 | 9.3 | 9.4 | 0 | 9.2 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6530.0924 | 0 | 6375.4273 | 6534.3557 | 6609.6998 | 6987.2425 | 6794.9192 | 0 | 6727.8984 | 0 | 6410.9931
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.84 | 0.84 | 0.81 | 0.83 | 0.88 |  | 0.81 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 |  | 36.5 | 36.3 | 36.4 | 36.3 | 36.4 |  | 35.7 |  | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.5 |  | 37.4 | 37.1 | 37.1 | 36.9 | 36.8 |  | 36.1 |  | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.7 | 1 | 3.1 | 2.8 | 2.1 | 2.9 | 2.3 | 0 | 1.4 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.6 |  | 29.4 | 29 | 29.5 | 28.8 | 29.5 |  | 29.2 |  | 29.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.8 |  | 34.3 | 34.3 | 35 | 34 | 34.5 |  | 34.7 |  | 34.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 0 | 4.9 | 5.3 | 5.5 | 5.2 | 5 | 0 | 5.5 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1296.9 |  | 1295.5 | 1298.5 | 1293.3 | 1295.14 | 1295.9 |  | 1291.7 |  | 1295.9
| HEAT CAPACITY | kW | 8226.9 | 0 | 7787.3903 | 0 | 7330.1963 | 7946.94 | 8213.7991 | 7776.8222 | 7482.1016 | 0 | 8203.6374 | 0 | 8080.6697
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.46 | 0.46 | 0.47 | 0.47 |  | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 |  | 19.5 | 19.7 | 19.8 | 19.8 | 20 |  | 19.2 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 195.9 |  | 128.7 | 206.6 | 202.3 | 201.6 | 205.9 |  | 161.2 |  | 191.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 6.1 |  | 5.66 | 5.67 | 5.66 | 5.73 | 5.81 |  | 5.65 |  | 5.26
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 24
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-24
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 70.3 | 70.3 |  | 75.5 |  | 73.3 |  | 74.4 | 72.7 | 74.3 |  | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.8 | 0.8 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 64.6 | 64.5 |  | 71.1 |  | 67.1 |  | 70 | 67.3 | 69.1 |  | 69.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.2 | 69.3 |  | 70.7 |  | 65.4 |  | 67.9 | 74.7 | 75 |  | 72.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 35.2 | 37.5 |  | 50.8 |  | 37.1 |  | 35.7 | 49.8 | 54.6 |  | 45.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 117.1 | 116.3 |  | 115.3 |  | 116.4 |  | 117 | 117.8 | 117.4 |  | 119.4
| INPUT | Kw | 1194kW | 1147 | 1156 |  | 1172 |  | 1166 |  | 1178 | 1197 | 1183 |  | 1201
COMPRESSOR | RUNNING TIME | Hr | NA | 50498.8 | 50487.9 |  | 51519 |  | 49422.1 |  | 51850.2 | 51025.8 | 51015 |  | 50890.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.1 |  | 59.2 |  | 58.1 |  | 57.3 | 58.9 | 58.7 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.53 |  | 0.46 |  | 0.58 |  | 0.52 | 0.48 | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 45.1 |  | 44.9 |  | 45 |  | 45.1 | 44.9 | 45.1 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.25 | 0.23 |  | 0.22 |  | 0.22 |  | 0.22 | 0.23 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.2 | 4.4 |  | 3.6 |  | 3.9 |  | 3.8 | 4.8 | 4.1 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 3.9 | 3.7 |  | 2.8 |  | 3.2 |  | 2.8 | 3.2 | 3.3 |  | 3.5
| APPROACH TEMP | CELCIUS | C | 0.7 | 0.9 | 0 | 2.1 |  | 0.8 | 0 | 1.3 | 1.3 | 1 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 630.1 | 627 |  | 639.2 |  | 639.9 |  | 628.8 | 637.6 | 634.5 |  | 630.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.6 | 14.1 |  | 14.1 |  | 13 |  | 13.4 | 13.4 | 13.6 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.6 | 4.6 |  | 4.9 |  | 4 |  | 4.1 | 4.5 | 4.3 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9 | 9.5 | 0 | 9.2 | 0 | 9 | 0 | 9.3 | 8.9 | 9.3 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 6548.3834 | 6878.1755 | 0 | 6790.5774 | 0 | 6650.2309 | 0 | 6752.7021 | 6552.7021 | 6813.9145 | 0 | 6338.1409
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.83 | 0.81 |  | 0.83 |  | 0.82 |  | 0.82 | 0.82 | 0.82 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.5 | 35.8 |  | 36.1 |  | 35.9 |  | 35.9 | 36.3 | 35.2 |  | 35.9
| SATURATED TEMEPRATURE | CELCIUS | C | 37 | 36.2 |  | 37 |  | 36.6 |  | 36.4 | 36.7 | 35.6 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 1.7 | 1 | 3.2 | 0 | 2.1 | 0 | 2.3 | 1.5 | 1.6 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 30.1 | 29.1 |  | 29 |  | 29.1 |  | 29 | 29.8 | 28.8 |  | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 35.3 | 34.5 |  | 33.8 |  | 34.5 |  | 34.1 | 35.2 | 34 |  | 34.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.2 | 5.4 | 0 | 4.8 | 0 | 5.4 | 0 | 5.1 | 5.4 | 5.2 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1301.5 | 1297.1 |  | 1293.6 |  | 1296.1 |  | 1297.6 | 1295.7 | 1297.2 |  | 1291.3
| HEAT CAPACITY | kW | 8226.9 | 7815.0115 | 8088.1524 | 0 | 7170.0693 | 0 | 8081.9169 | 0 | 7641.7552 | 8079.4226 | 7789.1917 | 0 | 8051.9861
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.47 |  | 0.46 |  | 0.46 |  | 0.46 | 0.47 | 0.45 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 20.3 | 20.1 |  | 19.5 |  | 19.7 |  | 19.5 | 20.1 | 19 |  | 19.8
| LIQUID LEVEL | mm | mm | 192.4 | 206 |  | 124.7 |  | 204 |  | 207.5 | 161.6 | 159 |  | 195.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.92 | 5.89 |  | 5.58 |  | 5.73 |  | 5.83 | 5.59 | 5.78 |  | 5.48
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 25
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-25
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 69.2 |  | 77.4 | 73.8 | 73.4 | 76.7 | 76.7 |  | 74.6 |  | 72.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.9 |  | 0 | 0 | 0 | 0 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 62.6 |  | 72.7 | 69.8 | 68.3 | 72.7 | 72.7 |  | 69.3 |  | 66.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.4 |  | 70.8 | 64.3 | 63.2 | 67.2 | 67 |  | 75 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 34.8 |  | 50.9 | 38.2 | 38.6 | 35.2 | 35.1 |  | 50.3 |  | 42.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.8 |  | 116.3 | 116.2 | 115.4 | 119.5 | 119.3 |  | 117.7 |  | 117.8
| INPUT | Kw | 1194kW |  | 1131 |  | 1179 | 1201 | 1188 | 1224 | 1214 |  | 1200 |  | 1200
COMPRESSOR | RUNNING TIME | Hr | NA |  |  |  | 49431.8 | 49440.8 | 51859.8 | 51868.8 |  |  |  |  | 50898.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 |  | 59.2 | 57.9 | 57.8 | 57.3 | 57.4 |  | 58.9 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 | 0.59 | 0.52 |  | 0.49 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 |  | 45 | 44.9 | 44.9 | 45.1 | 45 |  | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.25 | 0.22 | 0.23 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.5 |  | 3.5 | 4.4 | 4.3 | 4.5 | 4 |  | 4.4 |  | 4.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.1 |  | 2.7 | 3.4 | 3.3 | 3.5 | 3 |  | 3.2 |  | 4
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0 | 2.4 |  | 0.8 | 1.1 | 1.3 | 0 | 1.4 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 637.3 |  | 631.9 | 626.7 | 630.1 | 710.5 | 636.2 |  | 639.5 |  | 631.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 14.1 |  | 13.9 | 13.7 | 13 | 13.4 | 13.7 |  | 13.6 |  | 13.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.9 |  | 5.1 | 4.6 | 4.1 | 4.6 | 4.3 |  | 4.6 |  | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.2 | 0 | 8.8 | 9.1 | 8.9 | 8.8 | 9.4 | 0 | 9 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6770.3926 | 0 | 6421.1547 | 6585.4157 | 6475.6236 | 7219.8614 | 6905.6351 | 0 | 6646.0739 | 0 | 6343.164
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 | 0.83 | 0.84 | 0.84 | 0.84 |  | 0.82 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.4 |  | 36.8 | 36.4 | 36.7 | 36.6 | 36.8 |  | 36.1 |  | 36.6
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.9 |  | 37.7 | 37.1 | 37.3 | 37.2 | 37.3 |  | 36.4 |  | 37.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.7 | 1 | 3.1 | 2.1 | 2 | 2.4 | 2.3 | 0 | 1.4 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.9 |  | 29.8 | 29.5 | 29.9 | 29.5 | 29.8 |  | 29.5 |  | 29.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 35.2 |  | 34.6 | 35 | 35.3 | 34.8 | 35 |  | 35 |  | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 0 | 4.8 | 5.5 | 5.4 | 5.3 | 5.2 | 0 | 5.5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1299.6 |  | 1299.8 | 1289.2 | 1296 | 129.1 | 1297.6 |  | 1298.3 |  | 1291.1
| HEAT CAPACITY | kW | 8226.9 | 0 | 7953.6721 | 0 | 7204.4342 | 8187.7598 | 8081.2933 | 790.1039 | 7791.5935 | 0 | 8245.5543 | 0 | 7752.5635
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 |  | 0.47 | 0.46 | 0.47 | 0.47 | 0.47 |  | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.5 |  | 19.7 | 19.7 | 20 | 20.1 | 20 |  | 19.7 |  | 20.6
| LIQUID LEVEL | mm | mm |  | 197.6 |  | 139.2 | 195 | 200.3 | 205 | 215.8 |  | 159.4 |  | 203.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.95 |  | 5.48 | 5.6 | 5.59 | 5.23 | 5.65 |  | 5.54 |  | 5.29
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 26
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-26
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.6 | 69.2 |  | 77.4 |  | 73.4 |  | 76.7 | 74.5 | 74.6 |  | 72.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.8 | 0.9 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.7 | 62.6 |  | 72.7 |  | 68.3 |  | 72.7 | 69.5 | 69.3 |  | 66.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 68.7 | 69.4 |  | 70.8 |  | 63.2 |  | 67 | 74.7 | 75 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 41.3 | 34.8 |  | 50.9 |  | 38.6 |  | 35.1 | 54 | 50.3 |  | 42.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 50.3 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 120.5 | 115.8 |  | 116.3 |  | 115.4 |  | 119.3 | 118.7 | 117.7 |  | 117.8
| INPUT | Kw | 1194kW | 1182 | 1131 |  | 1179 |  | 1188 |  | 1214 | 1213 | 1200 |  | 1200
COMPRESSOR | RUNNING TIME | Hr | NA | 50531.2 | 50522.2 |  | 49441.5 |  | 49451.5 |  | 51882.9 | 51058 | 51049 |  | 50909
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.8 | 58 |  | 59.2 |  | 57.8 |  | 57.4 | 58.8 | 58.9 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 | 0.48 | 0.49 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 44.9 |  | 45 |  | 44.9 |  | 45 | 44.9 | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.22 |  | 0.22 | 0.23 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.5 | 4.5 |  | 3.5 |  | 4.3 |  | 4 | 4.8 | 4.4 |  | 4.9
| SATURATION TEMPERATURE | CELCIUS | C | 4 | 4.1 |  | 2.7 |  | 3.3 |  | 3 | 3.1 | 3.2 |  | 4
| APPROACH TEMP | CELCIUS | C | 1 | 0.8 | 0 | 2.4 |  | 0.8 | 0 | 1.3 | 1.9 | 1.4 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 696.2 | 637.3 |  | 631.9 |  | 630.1 |  | 636.2 | 689.3 | 639.5 |  | 631.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.8 | 14.1 |  | 13.9 |  | 13 |  | 13.7 | 13.8 | 13.6 |  | 13.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5 | 4.9 |  | 5.1 |  | 4.1 |  | 4.3 | 5 | 4.6 |  | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.8 | 9.2 | 0 | 8.8 | 0 | 8.9 | 0 | 9.4 | 8.8 | 9 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 7074.5497 | 6770.3926 | 0 | 6421.1547 | 0 | 6475.6236 | 0 | 6905.6351 | 7004.4342 | 6646.0739 | 0 | 6343.164
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.83 | 0.83 |  | 0.85 |  | 0.84 |  | 0.84 | 0.82 | 0.82 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.4 | 36.4 |  | 36.8 |  | 36.7 |  | 36.8 | 36.1 | 36.1 |  | 36.6
| SATURATED TEMEPRATURE | CELCIUS | C | 37 | 36.9 |  | 37.7 |  | 37.3 |  | 37.3 | 36.4 | 36.4 |  | 37.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.7 | 1.7 | 1 | 3.1 | 0 | 2 | 0 | 2.3 | 1.5 | 1.4 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.7 | 29.9 |  | 29.8 |  | 29.9 |  | 29.8 | 29.5 | 29.5 |  | 29.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 35.3 | 35.2 |  | 34.6 |  | 35.3 |  | 35 | 34.9 | 35 |  | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 5.3 | 0 | 4.8 | 0 | 5.4 | 0 | 5.2 | 5.4 | 5.5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1303.2 | 1299.6 |  | 1299.8 |  | 1296 |  | 1297.6 | 1299.4 | 1298.3 |  | 1291.1
| HEAT CAPACITY | kW | 8226.9 | 8427.1594 | 7953.6721 | 0 | 7204.4342 | 0 | 8081.2933 | 0 | 7791.5935 | 8102.4942 | 8245.5543 | 0 | 7752.5635
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.48 |  | 0.47 |  | 0.47 |  | 0.47 | 0.47 | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C | 20.2 | 20.5 |  | 19.7 |  | 20 |  | 20 | 19.9 | 19.7 |  | 20.6
| LIQUID LEVEL | mm | mm | 188.7 | 197.6 |  | 139.2 |  | 200.3 |  | 215.8 | 156.9 | 159.4 |  | 203.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.49 | 5.95 |  | 5.48 |  | 5.59 |  | 5.65 | 5.36 | 5.54 |  | 5.29
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 27
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-27
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.4 |  | 81.3 | 74 | 72 | 74 | 70.4 |  | 78.5 |  | 74.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.4 |  | 0 | 0 | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.3 |  | 77.1 | 69.5 | 68.2 | 69.1 | 65 |  | 74.1 |  | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.5 |  | 70.4 | 63.7 | 64.7 | 67.9 | 66.5 |  | 74.8 |  | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 42 |  | 56 | 36.6 | 42.1 | 32.7 | 34.9 |  | 58.2 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.9 |  | 116.7 | 117.5 | 114.6 | 116.5 | 111.9 |  | 118.9 |  | 116.8
| INPUT | Kw | 1194kW |  | 1125 |  | 1175 | 1187 | 1153 | 1183 | 1133 |  | 1200 |  | 1179
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50230 |  | 51331.8 | 49471.1 | 49459.5 | 51904 | 51892.7 |  | 51073 |  | 50918.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 |  | 58.9 | 57.7 | 57.7 | 57.5 | 57.2 |  | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.48 | 0.59 | 0.58 | 0.52 | 0.52 |  | 0.57 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 |  | 45 | 45.1 | 45.1 | 45 | 45 |  | 45 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.21 |  | 0.21 | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 3.9 |  | 2.8 | 4 | 4 | 4 | 3.9 |  | 4 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.3 |  | 2 | 3.3 | 3.2 | 2.9 | 2.4 |  | 2.8 |  | 3.1
| APPROACH TEMP | CELCIUS | C | 0 | 1.3 | 0 | 2.4 | 0.7 | 1.3 | 1.3 | 1.6 | 0 | 1.2 | 0 | 1.3
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 646.56 |  | 630.56 | 632.5 | 639.52 | 627.7 | 643.68 |  | 633.12 |  | 633.52
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.3 |  | 13.2 | 13.1 | 13.5 | 13.2 | 13.5 |  | 13.2 |  | 13.1
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.4 | 4 | 4.5 | 4.2 | 4 |  | 4 |  | 4.4
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.7 | 0 | 8.8 | 9.1 | 9 | 9 | 9.5 | 0 | 9.2 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6495.4642 | 0 | 6407.5381 | 6646.3626 | 6646.2818 | 6523.4411 | 7061.1547 | 0 | 6725.9861 | 0 | 6364.4619
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 |  | 0.83 | 0.84 | 0.82 | 0.83 | 0.82 |  | 0.8 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 34.5 |  | 35 | 36.6 | 34.8 | 36.6 | 34.7 |  | 34.1 |  | 34.7
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36 |  | 36.9 | 37.3 | 36.5 | 37 | 36.3 |  | 35.5 |  | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.4 | 1 | 3.6 | 2.1 | 2.9 | 2.2 | 3 | 0 | 2.3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.4 |  | 28.3 | 29.8 | 28.3 | 29.6 | 28.1 |  | 28.3 |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.6 |  | 33.3 | 35.2 | 33.6 | 34.8 | 33.3 |  | 33.2 |  | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 0 | 5 | 5.4 | 5.3 | 5.2 | 5.2 | 0 | 4.9 | 0 | 5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1291.5 |  | 1296.82 | 1298.6 | 1293.6 | 1296 | 1293.18 |  | 1299.9 |  | 1295.7
| HEAT CAPACITY | kW | 8226.9 | 0 | 7754.9654 | 0 | 7487.4134 | 8097.5058 | 7916.9515 | 7781.9861 | 7765.0531 | 0 | 7355.0924 | 0 | 7480.9469
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.45 |  | 0.44 | 0.46 | 0.45 | 0.47 | 0.45 |  | 0.44 |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C |  | 18.9 |  | 18.2 | 19.8 | 19 | 20 | 19.1 |  | 18.1 |  | 18.9
| LIQUID LEVEL | mm | mm |  | 201.7 |  | 117.8 | 205.4 | 200.8 | 197.4 | 206.4 |  | 160 |  | 199.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.54 |  | 5.72 | 5.63 | 5.9 | 5.66 | 5.68 |  | 5.68 |  | 5.33
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 28
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-28
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 68.5 | 67.8 |  | 75.2 |  | 74 |  | 74 | 70.5 | 73.4 |  | 72.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.1 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 62.6 | 60.7 |  | 69.6 |  | 69.5 |  | 69.1 | 64.5 | 68.7 |  | 66.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.2 | 69.4 |  | 70.9 |  | 63.7 |  | 67.6 | 75.1 | 73.5 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 35.5 | 37.4 |  | 49.1 |  | 36.1 |  | 34.6 | 50.7 | 50 |  | 43
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 116.7 | 115.3 |  | 113.8 |  | 118 |  | 116.9 | 115.6 | 117.5 |  | 117.3
| INPUT | Kw | 1194kW | 1145 | 1148 |  | 1164 |  | 1205 |  | 1190 | 1172 | 1199 |  | 1192
COMPRESSOR | RUNNING TIME | Hr | NA | 50566.6 | 50553.7 |  | 51556.4 |  | 49483.2 |  | 51916 | 51093.5 | 51080.7 |  | 50927.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.4 |  | 59.3 |  | 57.7 |  | 57.5 | 58.9 | 58.7 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 | 0.48 | 0.48 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 44.7 |  | 44.9 |  | 45 |  | 44.9 | 44.9 | 44.9 |  | 45.2
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.21 | 0.21 |  | 0.22 |  | 0.23 |  | 0.22 | 0.23 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.6 | 4.9 |  | 3.6 |  | 4.2 |  | 4 | 4.7 | 4.5 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 4.3 | 4.5 |  | 2.7 |  | 3.4 |  | 3 | 3.7 | 3.7 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0.7 | 0.8 | 0 | 2.2 | 0 | 0.6 | 0 | 1.4 | 1.1 | 0.9 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 643.4 | 677.7 |  | 629.3 |  | 641.2 |  | 619.8 | 638.9 | 634.9 |  | 638.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 14 | 13.9 |  | 13.5 |  | 13.1 |  | 13.6 | 13.6 | 13.9 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5 | 5.3 |  | 4.9 |  | 4 |  | 4.4 | 4.8 | 4.6 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9 | 8.6 | 0 | 8.6 | 0 | 9.1 | 0 | 9.2 | 8.8 | 9.3 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 6686.6051 | 6730.0462 | 0 | 6249.3995 | 0 | 6737.7829 | 0 | 6584.4804 | 6492.2864 | 6818.2102 | 0 | 6413.4873
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.84 | 0.83 |  | 0.85 |  | 0.84 |  | 0.84 | 0.82 | 0.82 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.8 | 36.5 |  | 36.8 |  | 36.8 |  | 36.7 | 36.5 | 36.1 |  | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C | 37.3 | 36.9 |  | 37.6 |  | 37.4 |  | 37.2 | 36.8 | 36.4 |  | 37.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.6 | 1.6 | 1 | 3.1 | 0 | 2.1 | 0 | 2.2 | 1.5 | 1.5 | 0 | 2.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 30.4 | 29.8 |  | 29.8 |  | 29.9 |  | 29.8 | 30.2 | 29.7 |  | 29.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 35.7 | 35.3 |  | 34.5 |  | 35.3 |  | 35 | 35.3 | 34.9 |  | 34.8
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.3 | 5.5 | 0 | 4.7 | 0 | 5.4 | 0 | 5.2 | 5.1 | 5.2 | 0 | 5.1
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1303.8 | 1291.4 |  | 1301 |  | 1296.7 |  | 1295.2 | 1298.6 | 1293.6 |  | 1297
| HEAT CAPACITY | kW | 8226.9 | 7979.3764 | 8201.7321 | 0 | 7060.8545 | 0 | 8085.6582 | 0 | 7777.1824 | 7647.6443 | 7767.5751 | 0 | 7638.2217
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.48 | 0.48 |  | 0.46 |  | 0.47 |  | 0.47 | 0.47 | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C | 20.7 | 20.7 |  | 19.9 |  | 19.9 |  | 20.1 | 20.3 | 19.2 |  | 20.3
| LIQUID LEVEL | mm | mm | 204.7 | 196.5 |  | 127.5 |  | 212.7 |  | 214.8 | 158 | 160 |  | 199
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.82 | 5.52 |  | 5.49 |  | 5.54 |  | 5.82 | 5.56 | 5.6 |  | 5.29
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 29
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-29
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 68.5 |  | 76.5 | 74.3 | 74.7 | 75.8 | 76.1 |  | 76 |  | 72.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 62.5 |  | 72.2 | 68.8 | 70.3 | 73 | 70.9 |  | 71.3 |  | 66.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.4 |  | 70.2 | 65.3 | 64.3 | 68.6 | 66.1 |  | 74.4 |  | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 38.5 |  | 59.2 | 38.9 | 37.4 | 36.7 | 35.8 |  | 53 |  | 43.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.1 |  | 115.8 | 113.5 | 117 | 117.4 | 117.2 |  | 118.4 |  | 116.4
| INPUT | Kw | 1194kW |  | 1138 |  | 1175 | 1174 | 1198 | 1207 | 1197 |  | 1210 |  | 1185
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50577.9 |  | 51566.2 | 49503.6 | 49492.9 | 51986.2 | 51925.9 |  | 51104.8 |  | 50936.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59.2 | 57.8 | 57.9 | 57.3 | 57.6 |  | 58.6 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.58 | 0.59 | 0.59 | 0.59 |  | 0.46 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.2 |  | 45 | 57.8 | 44.9 | 44.9 | 45 |  | 44.9 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.24 |  | 0.22 | 0.22 | 0.23 | 0.22 | 0.23 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 |  | 3.6 | 4 | 4.1 | 4.4 | 3.9 |  | 4.6 |  | 4.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.4 |  | 2.8 | 3.1 | 3.3 | 3.3 | 3.2 |  | 3.6 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0 | 0.6 | 0 | 2.2 | 1.4 | 1.2 | 1.3 | 1.1 | 0 | 1.1 | 0 | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 671.44 |  | 630.48 | 638.8 | 632.32 | 709 | 635.6 |  | 655.52 |  | 633.52
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.6 |  | 13.7 | 13.6 | 13.5 | 13.5 | 13.8 |  | 13.8 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 |  | 5 | 4.5 | 4.5 | 4.6 | 4.3 |  | 4.7 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.6 | 0 | 8.7 | 9.1 | 9 | 8.9 | 9.5 | 0 | 9.1 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6667.8799 | 0 | 6333.9215 | 6712.5635 | 6571.455 | 7286.4896 | 6972.5173 | 0 | 6888.2587 | 0 | 6364.4619
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.84 | 0.8 | 0.84 | 0.8 | 0.83 |  | 0.81 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 |  | 36.4 | 35.1 | 36.3 | 35.2 | 36.3 |  | 35.8 |  | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.5 |  | 37.4 | 35.8 | 37 | 35.8 | 37 |  | 36.2 |  | 36.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 2.4 | 1 | 3.8 | 2.1 | 2.7 | 2.3 | 3 | 0 | 2.2 | 0 | 2.7
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.9 |  | 28.7 | 28.7 | 28.8 | 28.1 | 28.7 |  | 28.8 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.1 |  | 33.6 | 33.7 | 34.3 | 33.5 | 34 |  | 34 |  | 34.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 0 | 4.9 | 5 | 5.5 | 5.4 | 5.3 | 0 | 5.2 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1292.76 |  | 1298.92 | 1292 | 1298.08 | 1293.1 | 1290.1 |  | 1287.3 |  | 1296.82
| HEAT CAPACITY | kW | 8226.9 | 0 | 7762.5312 | 0 | 7349.5473 | 7459.5843 | 8244.157 | 8063.2102 | 7895.5312 | 0 | 7729.746 | 0 | 7786.9099
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.45 | 0.46 | 0.45 | 0.46 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 |  | 19.7 | 19 | 19.5 | 19.2 | 19.9 |  | 19.5 |  | 20.3
| LIQUID LEVEL | mm | mm |  | 202.3 |  | 130.3 | 207.3 | 205.9 | 210.5 | 207.2 |  | 162.2 |  | 202.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.75 |  | 5.48 | 5.87 | 5.61 | 5.28 | 5.59 |  | 5.57 |  | 5.46
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 30
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-30
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 69.9 | 69.2 |  | 77.4 |  | 73.4 |  | 76.7 | 78.3 | 74.6 |  | 72.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.9 |  | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 65.7 | 62.6 |  | 72.7 |  | 68.3 |  | 72.7 | 74.1 | 69.3 |  | 66.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 67.8 | 69.4 |  | 70.8 |  | 63.2 |  | 67 | 73.2 | 75 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 39.8 | 34.8 |  | 50.9 |  | 38.6 |  | 35.1 | 53.3 | 50.3 |  | 42.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 606 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 117 | 115.8 |  | 116.3 |  | 115.4 |  | 119.3 | 120.3 | 117.7 |  | 117.8
| INPUT | Kw | 1194kW | 1141 | 1131 |  | 1179 |  | 1188 |  | 1214 | 1219 | 1200 |  | 1200
COMPRESSOR | RUNNING TIME | Hr | NA | 50598.1 | 50588.4 |  | 51577 |  | 49514.8 |  | 51944.6 | 51125.2 | 51115.5 |  | 50947.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58 |  | 59.2 |  | 57.8 |  | 57.4 | 58.7 | 58.9 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 | 0.47 | 0.49 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 44.9 |  | 45 |  | 44.9 |  | 45 | 44.8 | 44.9 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.22 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.2 | 4.5 |  | 3.5 |  | 4.3 |  | 4 | 4.2 | 4.4 |  | 4.9
| SATURATION TEMPERATURE | CELCIUS | C | 3.7 | 4.1 |  | 2.7 |  | 3.3 |  | 3 | 3.3 | 3.2 |  | 4
| APPROACH TEMP | CELCIUS | C | 1.1 | 0.2 | 0 | 1.4 |  | 1 | 0 | 1.1 | 1.1 | 0.7 | 0 | 0.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 698.4 | 649.52 |  | 634.08 |  | 632.4 |  | 653.12 | 689.1 | 632.48 |  | 634.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.3 | 13.1 |  | 12.8 |  | 13.3 |  | 13.4 | 13.2 | 13.1 |  | 12.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.8 | 4.3 |  | 4.1 |  | 4.3 |  | 4.1 | 4.4 | 3.9 |  | 4.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.5 | 8.8 | 0 | 8.7 | 0 | 9 | 0 | 9.3 | 8.8 | 9.2 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 6854.9654 | 6600.2032 | 0 | 6370.0878 | 0 | 6572.2864 | 0 | 7013.8753 | 7002.4018 | 6719.1871 | 0 | 6373.3025
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.8 |  | 0.82 |  | 0.81 |  | 0.81 | 0.81 | 0.79 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.4 | 36.4 |  | 36.8 |  | 36.7 |  | 36.8 | 35.2 | 36.1 |  | 36.6
| SATURATED TEMEPRATURE | CELCIUS | C | 35.9 | 35.6 |  | 36.4 |  | 36 |  | 36 | 35.6 | 35.2 |  | 36.1
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 1.6 | 2.4 | 1 | 1.8 | 0 | 2.8 | 0 | 3 | 1.5 | 2.3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.8 | 27.9 |  | 27.8 |  | 27.9 |  | 27.7 | 28.5 | 27.9 |  | 28.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.3 | 33.2 |  | 34.6 |  | 33.2 |  | 33 | 34.1 | 32.9 |  | 33.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.3 | 0 | 6.8 | 0 | 5.3 | 0 | 5.3 | 5.6 | 5 | 0 | 5.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1291.4 | 1292.76 |  | 1301.16 |  | 1292.76 |  | 1295 | 1300.4 | 1288.36 |  | 1294.72
| HEAT CAPACITY | kW | 8226.9 | 8201.7321 | 7911.8106 | 0 | 10216.9607 | 0 | 7911.8106 | 0 | 7925.5196 | 8409.0531 | 7438.5681 | 0 | 7774.3002
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.48 |  | 0.47 |  | 0.47 |  | 0.47 | 0.45 | 0.46 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C | 19.7 | 20.5 |  | 19.7 |  | 20 |  | 20 | 18.8 | 19.7 |  | 20.6
| LIQUID LEVEL | mm | mm | 196.1 | 197.6 |  | 139.2 |  | 200.3 |  | 215.8 | 159.4 | 159.4 |  | 203.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.48 | 5.95 |  | 5.48 |  | 5.59 |  | 5.65 | 5.35 | 5.54 |  | 5.29
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 31
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2025-05-31
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.3 |  | 75.2 | 74 | 74.6 | 74.6 | 76.7 |  | 76.8 |  | 75.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.8 |  | 0 | 0 | 0 | 0 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.5 |  | 69.6 | 70.2 | 69.5 | 71.2 | 72.7 |  | 71.7 |  | 69.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 69.3 |  | 70.9 | 64.1 | 64 | 67.6 | 67 |  | 74.7 |  | 72.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 37.5 |  | 49.1 | 40.9 | 38.8 | 36.6 | 35.1 |  | 55.4 |  | 45.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.3 |  | 113.8 | 117.5 | 117.2 | 116.5 | 119.3 |  | 119.4 |  | 119.4
| INPUT | Kw | 1194kW |  | 1156 |  | 1164 | 1182 | 1193 | 1186 | 1214 |  | 1200 |  | 1201
COMPRESSOR | RUNNING TIME | Hr | NA |  | 50607.1 |  | 51586.6 | 49533.2 | 49524.3 | 51963.2 | 51954.2 |  | 51137.8 |  | 50956.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59.3 | 57.8 | 57.7 | 57.5 | 57.4 |  | 58.7 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.58 | 0.52 | 0.52 |  | 0.48 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 44.9 | 46.1 | 44.9 | 44.8 | 45 |  | 44.9 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.6 | 4 | 4 | 4 | 4 |  | 4.3 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.7 |  | 2.7 | 3.4 | 3.4 | 3 | 3 |  | 3.2 |  | 3.5
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 0 | 2.2 | 1.2 | 1.3 | 1.1 | 1.3 | 0 | 1.4 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 627 |  | 629.3 | 633.04 | 635.28 | 632.08 | 636.2 |  | 648.6 |  | 630.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 14.1 |  | 13.5 | 13.5 | 13.6 | 13.6 | 13.7 |  | 13.8 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 |  | 4.9 | 4.6 | 4.7 | 4.1 | 4.3 |  | 4.6 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.5 | 0 | 8.6 | 8.9 | 8.9 | 9.5 | 9.4 | 0 | 9.2 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6878.1755 | 0 | 6249.3995 | 6505.8383 | 6528.8591 | 6933.903 | 6905.6351 | 0 | 6890.4388 | 0 | 6338.1409
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 |  | 0.85 | 0.83 | 0.84 | 0.82 | 0.84 |  | 0.8 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.8 |  | 36.8 | 36 | 35.7 | 36 | 36.8 |  | 35 |  | 35.9
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.2 |  | 37.6 | 36.8 | 37.4 | 36.6 | 37.3 |  | 35.6 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS | 0-3 | 0 | 1.7 | 1 | 3.1 | 2.9 | 2.9 | 3 | 2.3 | 0 | 1.7 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.1 |  | 29.8 | 28.5 | 29.2 | 28.4 | 29.8 |  | 28.5 |  | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.5 |  | 34.5 | 33.9 | 34.5 | 33.6 | 35 |  | 33.9 |  | 34.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.4 | 0 | 4.7 | 5.4 | 5.3 | 5.2 | 5.2 | 0 | 5.4 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1297.1 |  | 1301 | 1291.92 | 1299.2 | 1291.5 | 1297.6 |  | 1292.9 |  | 1291.3
| HEAT CAPACITY | kW | 8226.9 | 0 | 8088.1524 | 0 | 7060.8545 | 8055.8522 | 7951.224 | 7754.9654 | 7791.5935 | 0 | 8061.963 | 0 | 8051.9861
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.46 | 0.46 | 0.46 | 0.47 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 |  | 19.9 | 19.3 | 19.1 | 19.5 | 20 |  | 19.3 |  | 19.8
| LIQUID LEVEL | mm | mm |  | 206 |  | 127.5 | 206.9 | 210.2 | 214.6 | 215.8 |  | 160 |  | 195.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.89 |  | 5.49 | 5.7 | 5.64 | 5.78 | 5.65 |  | 5.75 |  | 5.48
% OF COOLING CAPACITY | [12 empty] | 5.75
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO