## 1
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 70 |  | 77.1 | 74.6 | 72.7 | 76.1 | 73.3 | 76.7 | 73.4 |  | 79.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.3
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.3 |  | 72.2 | 69.4 | 66.9 | 70.7 | 67.5 | 72.3 | 70.3 |  | 75.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 64.7 |  | 66.8 | 61.3 | 63.3 | 63.4 | 65.2 | 69.1 | 70.8 |  | 72.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 56.9 |  | 51.3 | 37.6 | 39.5 | 35.1 | 32.3 | 52.8 | 48.1 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.4 |  | 116.5 | 116.1 | 115.6 | 117.3 | 116.4 | 116.7 | 117.6 |  | 119.4
| INPUT | Kw | 1194kW |  | 1153 |  | 1177 | 1194 | 1171 | 1205 | 1178 | 1197 | 1189 |  | 1208
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46525.3 |  | 47419.5 | 45004.6 | 44996 | 47303.2 | 47294.6 | 46640.1 | 46631.5 |  | 48519.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.8 |  | 58.9 | 57.6 | 57.5 | 57.2 | 57.5 | 58.5 | 58.6 |  | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 | 0.59 | 0.59 | 0.52 | 0.52 | 0.47 | 0.48 |  | 0.47
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 |  | 45.1 | 45.3 | 45.1 | 44.9 | 45 | 45.2 | 45.1 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 |  | 3.3 | 3.9 | 3.9 | 4.2 | 3.9 | 3.7 | 3.9 |  | 3.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.5 |  | 2.5 | 3.2 | 3.3 | 3.3 | 3.3 | 2.3 | 2.7 |  | 2.9
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0 | 2.1 | 1.1 | 0.8 | 1 | 0.8 | 1.3 | 1.5 | 0 | 1.6
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 654.1 |  | 646.4 | 670.96 | 643.39 | 746.48 | 661.6 | 669.84 | 636.3 |  | 643.1
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.1 |  | 13 | 12.7 | 12.9 | 12.4 | 12.9 | 12 | 13.1 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.3 |  | 4.6 | 4.3 | 4.1 | 4.3 | 4.1 | 3.6 | 4.2 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.8 | 0 | 8.4 | 8.4 | 8.8 | 8.1 | 8.8 | 8.4 | 8.9 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6646.7436 | 0 | 6269.9307 | 6508.157 | 6537.9122 | 6982.0878 | 6722.9561 | 6497.2933 | 6539.3418 | 0 | 6534.9654
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.85 | 0.83 | 0.83 | 0.85 | 0.81 | 0.82 | 0.83 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.1 |  | 36.7 | 36.2 | 36.3 | 36.9 | 36.8 | 35.8 | 36.4 |  | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.6 |  | 37.7 | 37 | 37 | 37.5 | 37.2 | 36.3 | 36.8 |  | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.5 | 0 | 4.3 | 3.7 | 2.9 | 4.4 | 3.5 | 3.3 | 2.2 | 0 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.6 |  | 28.6 | 28 | 28.7 | 27.9 | 28.5 | 27.9 | 28.5 |  | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.1 |  | 33.4 | 33.3 | 34.1 | 33.1 | 33.7 | 33 | 34.6 |  | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 4.8 | 5.3 | 5.4 | 5.2 | 5.2 | 5.1 | 6.1 | 0 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1300.8 |  | 1295.4 | 1298.08 | 1292.2 | 1292.34 | 1284.1 | 1236.34 | 1111.9 |  | 1295.3
| HEAT CAPACITY | kW | 8226.9 | 0 | 8261.4319 | 0 | 7180.0462 | 7944.3695 | 8057.5982 | 7760.0092 | 7710.5312 | 7280.9861 | 7832.0901 | 0 | 8525.6467
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.46 | 0.46 | 0.46 | 0.47 | 0.47 | 0.45 | 0.46 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.9 |  | 19.7 | 19.2 | 19.8 | 20.2 | 20.2 | 18.9 | 19.4 |  | 19.5
| LIQUID LEVEL | mm | mm |  | 185.3 |  | 117.5 | 201.1 | 201 | 218.9 | 206.3 | 160.8 | 160.5 |  | 199
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.47 |  | 5.4 | 5.3 | 5.6 | 5.06 | 5.4 | 5.4 | 5.65 |  | 5.27
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 2
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 71.2 |  | 77.7 |  | 70.4 |  | 73.3 |  | 74.3 |  | 78.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.2 |  | 72.8 |  | 66.1 |  | 70.6 |  | 69.7 |  | 73.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 64.7 |  | 67.2 |  | 63.6 |  | 63.5 |  | 68.1 |  | 72.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 56 |  | 51.3 |  | 38.7 |  | 30.9 |  | 50.4 |  | 42.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.6 |  | 117.7 |  | 116.4 |  | 118 |  | 116.9 |  | 119.7
| INPUT | Kw | 1194kW |  | 1132 |  | 1186 |  | 1176 |  | 1194 |  | 1185 |  | 1205
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46534.4 |  | 47428.9 |  | 45019.8 |  | 47318.4 |  | 46647.5 |  | 48529.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59.3 |  | 57.7 |  | 57.3 |  | 58.5 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 |  | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 |  | 44.8 |  | 45.1 |  | 45 |  | 44.8 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 |  | 0.22 |  | 2.2
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 |  | 3.6 |  | 4.3 |  | 4.1 |  | 3.9 |  | 4
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.7 |  | 2.7 |  | 3.6 |  | 2.9 |  | 2.7 |  | 3.2
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | 2.3 | 0 | 0.7 | 0 | 1.3 | 0 | 1.2 | 0 | 1.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 669.2 |  | 650.3 |  | 648.9 |  | 653.5 |  | 638.1 |  | 655.2
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.4 |  | 13.3 |  | 13.1 |  | 12.9 |  | 12.8 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 |  | 5 |  | 4.3 |  | 4.2 |  | 3.9 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.7 | 0 | 8.3 | 0 | 8.8 | 0 | 8.7 | 0 | 8.9 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6722.9099 | 0 | 6232.6674 | 0 | 6593.903 | 0 | 6565.1848 | 0 | 6557.8406 | 0 | 6582.2633
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.86 |  | 0.84 |  | 0.85 |  | 0.82 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.4 |  | 37.1 |  | 36.6 |  | 37.2 |  | 36.7 |  | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 37 |  | 38 |  | 37.3 |  | 37.6 |  | 37 |  | 36.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.6 | 0 | 4.1 | 0 | 2.8 | 0 | 3.5 | 0 | 2.2 | 0 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.1 |  | 28.8 |  | 29 |  | 28.9 |  | 28.8 |  | 28.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.4 |  | 33.9 |  | 34.5 |  | 34.1 |  | 34.8 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 0 | 5.1 | 0 | 5.5 | 0 | 5.2 | 0 | 6 | 0 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1297.3 |  | 1300.9 |  | 1303.2 |  | 1289.9 |  | 1110 |  | 1291.6
| HEAT CAPACITY | kW | 8226.9 | 0 | 7939.5958 | 0 | 7661.1894 | 0 | 8276.6744 | 0 | 7745.358 | 0 | 7690.5312 | 0 | 8203.0023
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.47 |  | 0.46 |  | 0.47 |  | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 |  | 19.9 |  | 19.8 |  | 20.1 |  | 19.6 |  | 20
| LIQUID LEVEL | mm | mm |  | 229.9 |  | 120.8 |  | 207.3 |  | 203.6 |  | 159.4 |  | 201.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.74 |  | 5.18 |  | 5.52 |  | 5.39 |  | 5.54 |  | 5.32
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 3
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.4 |  | 77.7 | 75.4 | 71.1 | 73.6 | 74.5 | 73.6 | 76 |  | 76.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.4 |  | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 |  | 0.3
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.9 |  | 74.2 | 70 | 65.1 | 70.3 | 69.3 | 70.6 | 71 |  | 71.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.7 |  | 68.5 | 62.9 | 63.9 | 63.9 | 64.7 | 71.1 | 73 |  | 74.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.1 |  | 51.4 | 41.3 | 38.3 | 31.7 | 34.7 | 56.8 | 50.2 |  | 41.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.1 |  | 117.6 | 116.4 | 115.5 | 118 | 117.8 | 116.6 | 119.1 |  | 117.7
| INPUT | Kw | 1194kW |  | 1144 |  | 1185 | 1206 | 1158 | 1198 | 1188 | 1188 | 1207 |  | 1189
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46554.7 |  | 47453.3 | 45038.6 | 45029.8 | 47337.3 | 47328.5 | 46667.4 | 46658.6 |  | 48547.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.2 | 57.8 | 57.4 | 57.9 | 57.3 | 58.6 | 58.6 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 | 0.52 | 0.52 | 0.48 | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 44.9 | 44.9 | 45 | 44.9 | 45 | 44.9 | 45.1 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.22 | 0.23 | 0.22 | 0.22 | 0.22 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.3 | 4.3 | 4.1 | 3.8 | 3.9 | 4.2 | 4.1 |  | 4
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.4 | 3.3 | 3.5 | 3.4 | 3.9 | 3.6 | 3.7 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 0 | 2.3 | 0.9 | 0.6 | 0.8 | 0.2 | 0.7 | 0.6 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 667.4 |  | 650.3 | 647.8 | 644.3 | 639.2 | 633.9 | 659.9 | 641 |  | 646.3
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.2 |  | 13.3 | 13.2 | 13 | 13.2 | 13.3 | 13.2 | 13.5 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 |  | 4.7 | 4.2 | 4.1 | 4.2 | 4.1 | 4.3 | 4.3 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.5 | 0 | 8.6 | 9 | 8.9 | 9 | 9.2 | 8.9 | 9.2 | 0 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6550.6928 | 0 | 6457.9446 | 6732.3326 | 6621.5589 | 6642.9561 | 6734.2725 | 6781.8822 | 6809.6998 | 0 | 6418.2217
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 | 0.82 | 0.83 | 0.84 | 0.84 | 0.83 | 0.83 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 |  | 36.9 | 35.8 | 36.4 | 37 | 36.9 | 35.7 | 36.5 |  | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.8 |  | 37.8 | 36.6 | 37 | 37.8 | 37.4 | 36 | 36.9 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.5 | 0 | 4.3 | 3 | 2.8 | 3.9 | 3.6 | 2.4 | 2.3 | 0 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.8 |  | 28.7 | 27.9 | 28.8 | 27.9 | 28.8 | 27.8 | 28.5 |  | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.3 |  | 33.5 | 33.6 | 34.2 | 33.9 | 33.8 | 33.6 | 34.6 |  | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 4.8 | 5.7 | 5.4 | 6 | 5 | 5.8 | 6.1 | 0 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1296.6 |  | 1302.5 | 1296.1 | 1300.6 | 1291 | 1287.2 | 1110 | 1106.1 |  | 1293.2
| HEAT CAPACITY | kW | 8226.9 | 0 | 8234.7575 | 0 | 7219.3995 | 8530.9122 | 8109.9769 | 8944.5727 | 7431.8707 | 7434.1801 | 7791.2356 | 0 | 8511.8245
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 | 0.45 | 0.47 | 0.47 | 0.47 | 0.45 | 0.46 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 |  | 19.5 | 19.2 | 20.2 | 19.9 | 20.2 | 19.5 | 19.7 |  | 19.8
| LIQUID LEVEL | mm | mm |  | 176.3 |  | 131.3 | 197.8 | 202.4 | 198.1 | 196.5 | 159.9 | 163.1 |  | 203.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.6 |  | 5.27 | 5.54 | 5.64 | 5.61 | 5.67 | 5.48 | 5.67 |  | 5.31
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 4
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 70.4 |  | 78.7 | 75.8 | 74.1 |  | 74.1 | 73.7 | 72.8 | 76.6 | 76.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.4 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0.3 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.9 |  | 74.4 | 70 | 38.4 |  | 38.4 | 70.9 | 68 | 72 | 71.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.7 |  | 68.2 | 63.6 | 63 |  | 63 | 71.4 | 72.6 | 73.6 | 72.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.1 |  | 46.7 | 42.3 | 38.1 |  | 38.1 | 56.3 | 49.8 | 44.5 | 39.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 117.1 |  | 117 | 116.4 | 117.8 |  | 117.8 | 116.6 | 117.8 | 116.1 | 117.5
| INPUT | Kw | 1194kW |  | 1144 |  | 1192 | 1205 | 1192 |  | 1192 | 1189 | 1195 | 1182 | 1201
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46554.7 |  | 47410.4 | 45056 | 44986.5 |  | 44986.5 | 46681.3 | 46613.8 | 48564.7 | 48503.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.2 | 57.8 | 57.6 |  | 57.6 | 58.5 | 58.9 | 59.3 | 59.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.59 | 0.48 | 0.48 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 45 | 44.9 | 44.9 |  | 44.9 | 44.8 | 44.9 | 44.8 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.23 | 0.22 | 0.22 | 0.22 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 |  | 3.4 | 4.3 | 4.2 |  | 4.2 | 4.2 | 4.4 | 4.1 | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.6 | 3.3 | 3.5 |  | 3.5 | 3.6 | 3.4 | 3.2 | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 0 | 2.3 | 0.8 | 0.7 | 0 | 0.7 | 0.8 | 1.2 | 1.7 | 1.4
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 667.4 |  | 648 | 647.8 | 638.5 |  | 638.5 | 663.4 | 641.8 | 675.3 | 648.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.2 |  | 13.4 | 13.1 | 13.2 |  | 13.2 | 13.1 | 13.4 | 13.2 | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 |  | 4.9 | 4.1 | 4.2 |  | 4.2 | 4.4 | 4.6 | 4.9 | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.5 | 0 | 8.5 | 9 | 9 | 0 | 9 | 8.7 | 8.8 | 8.3 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6550.6928 | 0 | 6360.2771 | 6732.3326 | 6635.6813 | 0 | 6635.6813 | 6664.642 | 6521.7552 | 6472.2748 | 6291.2702
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.87 | 0.82 | 0.85 |  | 0.85 | 0.84 | 0.83 | 0.8 | 0.48
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 |  | 37.5 | 35.8 | 37.2 |  | 37.2 | 35.7 | 37.2 | 35.6 | 37
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.8 |  | 38.4 | 36.6 | 37.8 |  | 37.8 | 36 | 37.5 | 35.7 | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.5 | 0 | 4.2 | 3 | 2.8 | 0 | 2.8 | 2.4 | 2.2 | 2.3 | 2.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.8 |  | 29.4 | 28 | 29.5 |  | 29.5 | 27.7 | 29.2 | 27.7 | 29.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.3 |  | 34.2 | 33.6 | 35 |  | 35 | 33.6 | 35.3 | 33.4 | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 4.8 | 5.6 | 5.5 | 0 | 5.5 | 5.9 | 6.1 | 5.7 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1296.6 |  | 1303.6 | 1294.3 | 1301.2 |  |  | 1187.6 | 1108.6 | 1297.8 | 1290
| HEAT CAPACITY | kW | 8226.9 | 0 | 8234.7575 | 0 | 7225.4965 | 8369.6074 | 8263.9723 | 0 | 0 | 8091.0393 | 7808.8453 | 8542.1016 | 8490.7621
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.47 | 0.45 | 0.47 |  | 0.47 | 0.45 | 0.47 | 0.46 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 |  | 20.1 | 19 | 20.3 |  | 20.3 | 19.1 | 20.3 | 19.5 | 20.3
| LIQUID LEVEL | mm | mm |  | 176.3 |  | 123.9 | 196.5 | 202.4 |  | 202.4 | 158.6 | 159.8 | 197.2 | 202.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.6 |  | 5.4 | 5.53 | 5.57 |  | 5.57 | 5.49 | 5.44 | 5.24 | 5.23
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 5
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 73.8 | 71.4 | 80.6 | 76.7 |  | 70.8 | 76.1 | 73.5 |  | 73.4 |  | 77.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0.1 | 0.2 | 0 |  | 0 | 0 | 0.1 |  | 0 |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% | 68.4 | 66.2 | 77.7 | 71.4 |  | 67.8 | 70.7 | 68.7 |  | 68.5 |  | 73.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 62.8 | 66 | 61.9 | 68.8 |  | 62.8 | 63.4 | 65.4 |  | 72.4 |  | 74.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 68.4 | 44.8 | 51.4 | 48.8 |  | 36.8 | 35.1 | 30.6 |  | 48.7 |  | 39.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 115.5 | 117.9 | 117.1 | 116.9 |  | 115.8 | 117.3 | 115.5 |  | 117.2 |  | 118.6
| INPUT | Kw | 1194kW | 1132 | 1164 | 1188 | 1184 |  | 1172 | 1205 | 1177 |  | 1196 |  | 1204
COMPRESSOR | RUNNING TIME | Hr | NA | 46583.3 | 46572.9 | 47483.2 | 47471.5 |  | 45070.8 | 47371.9 | 47361.1 |  | 46687.1 |  | 48575.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 57.8 | 59.5 | 58.7 | 59 |  | 57.7 | 57.2 | 57.6 |  | 58.6 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 | 0.48 | 0.49 |  | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 46 | 45.1 | 45.2 |  | 45 | 44.9 | 44.9 |  | 45.2 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 | 0.21 | 0.22 |  | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.7 | 4.3 | 2.7 | 3.6 |  | 4.2 | 4.2 | 3.9 |  | 4.3 |  | 4.1
| SATURATION TEMPERATURE | CELCIUS | C | 3.5 | 3.8 | 1.8 | 2.8 |  | 3.6 | 3.3 | 2.8 |  | 3.3 |  | 3.2
| APPROACH TEMP | CELCIUS | C | 0.8 | 0.8 | 2.3 | 2 | 0 | 0.7 | 1 | 1.2 | 0 | 1.2 | 0 | 1.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 695.6 | 671.9 | 674.3 | 654.54 |  | 633 | 746.48 | 649.9 |  | 647.7 |  | 654.1
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.3 | 13.4 | 12.3 | 13.5 |  | 13.3 | 12.4 | 12.8 |  | 13.5 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 4.6 | 4.1 | 4.8 |  | 4.3 | 4.3 | 4 |  | 4.5 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8 | 8.8 | 8.2 | 8.7 | 0 | 9 | 8.1 | 8.8 | 0 | 9 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 6425.8661 | 6827.6212 | 6384.8268 | 6575.6328 | 0 | 6578.5219 | 6982.0878 | 6604.0647 | 0 | 6731.2933 | 0 | 6571.2125
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.83 | 0.84 | 0.85 |  | 0.84 | 0.85 | 0.84 |  | 0.83 |  | 0.48
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.9 | 36.3 | 36.4 | 36.9 |  | 36.5 | 36.9 | 36.9 |  | 36.6 |  | 36.4
| SATURATED TEMEPRATURE | CELCIUS | C | 35.9 | 36.9 | 37.2 | 37.9 |  | 37.2 | 37.5 | 37.4 |  | 37 |  | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 3.4 | 2.7 | 4.3 | 4.4 | 0 | 2.8 | 4.4 | 3.5 | 0 | 2.3 | 0 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.4 | 28.9 | 28 | 28.8 |  | 28.9 | 27.9 | 28.8 |  | 28.7 |  | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 32.5 | 34.2 | 32.9 | 33.5 |  | 34.4 | 33.1 | 33.9 |  | 34.7 |  | 34.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.1 | 5.3 | 4.9 | 4.7 | 0 | 5.5 | 5.2 | 5.1 | 0 | 6 | 0 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1291.36 | 1298.9 | 1299.6 | 1296.5 |  | 1298.1 | 1293.4 | 1287.1 |  | 1110.7 |  | 1293.8
| HEAT CAPACITY | kW | 8226.9 | 7605.0069 | 7949.388 | 7353.3949 | 7036.4319 | 0 | 8244.2841 | 7766.3741 | 7579.9192 | 0 | 7695.3811 | 0 | 8216.9746
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.47 | 0.45 | 0.47 |  | 0.47 | 0.47 | 0.47 |  | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 18.8 | 20.1 | 18.8 | 19.9 |  | 20 | 20.2 | 20.1 |  | 19.9 |  | 20
| LIQUID LEVEL | mm | mm | 200.3 | 173.4 | 126 | 129.8 |  | 202.2 | 218.9 | 207.3 |  | 155.2 |  | 200.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.69 | 5.4 | 5.21 | 5.3 |  | 5.72 | 5.06 | 5.59 |  | 5.49 |  | 5.22
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 6
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 72 |  | 75.1 |  | 73.9 |  | 74.1 |  | 72.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 |  | 0 |  | 0.1 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.9 |  | 70.1 |  | 68.7 |  | 69.1 |  | 67.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 64.2 |  | 66.1 |  | 63.1 |  | 63.8 |  | 69.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 48.1 |  | 53.8 |  | 39.9 |  | 33.7 |  | 55.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 118.3 |  | 116.4 |  | 115.9 |  | 117.2 |  | 116.4
| INPUT | Kw | 1194kW |  | 1156 |  | 1176 |  | 1182 |  | 1201 |  | 1192
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46596 |  | 47486 |  | 45079 |  | 47385 |  | 46696
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 |  | 59.1 |  | 57.9 |  | 57.1 |  | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 |  | 0.59 |  | 0.53 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.2 |  | 45.1 |  | 44.9 |  | 45.1 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 |  | 0.23 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.2 |  | 3.1 |  | 4.6 |  | 4.4 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.4 |  | 3.6 |  | 3.5 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 0 | 2.4 | 0 | 0.6 | 0 | 1.3 | 0 | 1.2 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 710.5 |  | 686 |  | 660.5 |  | 712.4 |  | 717.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.3 |  | 13.3 |  | 13.1 |  | 13.3 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 |  | 4.8 |  | 4.2 |  | 4.8 |  | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.6 | 0 | 8.5 | 0 | 8.9 | 0 | 8.5 | 0 | 8.3 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 7055.7737 | 0 | 6733.2564 | 0 | 6788.0485 | 0 | 6992.3788 | 0 | 6880.5658 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.8 |  | 0.84 |  | 0.82 |  | 0.83 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.5 |  | 36.4 |  | 35.8 |  | 37.1 |  | 36.1
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36 |  | 37.4 |  | 36.5 |  | 37.1 |  | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.2 | 0 | 4.5 | 0 | 2.8 | 0 | 3.5 | 0 | 2.4 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.3 |  | 28.1 |  | 28.1 |  | 28.1 |  | 28
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.8 |  | 32.9 |  | 33.7 |  | 33.6 |  | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 4.8 | 0 | 5.6 | 0 | 5.5 | 0 | 6.1 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1263.2 |  | 1309.7 |  | 1295.4 |  | 1241.6 |  | 1079.4
| HEAT CAPACITY | kW | 8226.9 | 0 | 8022.6328 | 0 | 7259.3072 | 0 | 8376.7206 | 0 | 7885.4503 | 0 | 7603.164 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.45 |  | 0.45 |  | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.6 |  | 19.2 |  | 19.3 |  | 20.2 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 192 |  | 127 |  | 204.5 |  | 199.1 |  | 151.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.35 |  | 5.15 |  | 5.56 |  | 5.18 |  | 5.13
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 7
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 71.1 | 72 |  | 75.1 |  | 73.9 | 72.4 | 74.1 | 72.9 | 72.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.6 |  | 0 |  | 0 | 0 | 0.1 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% | 66.2 | 66.9 |  | 70.1 |  | 68.7 | 69.6 | 69.1 | 69.1 | 67.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 63.1 | 64.2 |  | 66.1 |  | 63.1 | 64.1 | 63.8 | 69.2 | 69.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 41.1 | 48.1 |  | 53.8 |  | 39.9 | 33.2 | 33.7 | 49.3 | 55.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 115.7 | 118.3 |  | 116.4 |  | 115.9 | 118.8 | 117.2 | 116.5 | 116.4
| INPUT | Kw | 1194kW | 1133 | 1156 |  | 1176 |  | 1182 | 1201 | 1201 | 1179 | 1192
COMPRESSOR | RUNNING TIME | Hr | NA | 46616.8 | 46596 |  | 47486 |  | 45079 | 47405.4 | 47385 | 46731.1 | 46696
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 58 |  | 59.1 |  | 57.9 | 57.4 | 57.1 | 58.6 | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 |  | 0.49 |  | 0.59 | 0.52 | 0.53 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 45.2 |  | 45.1 |  | 44.9 | 44.9 | 45.1 | 45 | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.24 | 0.23 |  | 0.21 |  | 0.23 | 0.22 | 0.23 | 0.22 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.8 | 4.2 |  | 3.1 |  | 4.6 | 4.5 | 4.4 | 3.9 | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 3.2 | 3.8 |  | 2.4 |  | 3.6 | 3.6 | 3.5 | 2.9 | 3.8
| APPROACH TEMP | CELCIUS | C | 1.2 | 0.9 | 0 | 2.4 | 0 | 0.6 | 1.2 | 1.3 | 1.2 | 1.2 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 689.4 | 710.5 |  | 686 |  | 660.5 | 742 | 712.4 | 668.7 | 717.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.6 | 13.3 |  | 13.3 |  | 13.1 | 12.7 | 13.3 | 12.8 | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.4 | 4.7 |  | 4.8 |  | 4.2 | 4.8 | 4.8 | 4.1 | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.2 | 8.6 | 0 | 8.5 | 0 | 8.9 | 7.9 | 8.5 | 8.7 | 8.3 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 6527.806 | 7055.7737 | 0 | 6733.2564 | 0 | 6788.0485 | 6768.8222 | 6992.3788 | 6717.8868 | 6880.5658 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.8 |  | 0.84 |  | 0.82 | 0.84 | 0.83 | 0.83 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36 | 35.5 |  | 36.4 |  | 35.8 | 36.9 | 37.1 | 36 | 36.1
| SATURATED TEMEPRATURE | CELCIUS | C | 36.5 | 36 |  | 37.4 |  | 36.5 | 37.1 | 37.1 | 36.4 | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.5 | 2.2 | 0 | 4.5 | 0 | 2.8 | 3.3 | 3.5 | 2.4 | 2.4 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.5 | 28.3 |  | 28.1 |  | 28.1 | 28.6 | 28.1 | 28.4 | 28
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34 | 33.8 |  | 32.9 |  | 33.7 | 33.8 | 33.6 | 34 | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.5 | 0 | 4.8 | 0 | 5.6 | 5.2 | 5.5 | 5.6 | 6.1 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1294.1 | 1263.2 |  | 1309.7 |  | 1295.4 | 1295.5 | 1241.6 | 1195.1 | 1079.4
| HEAT CAPACITY | kW | 8226.9 | 8218.8799 | 8022.6328 | 0 | 7259.3072 | 0 | 8376.7206 | 7778.9838 | 7885.4503 | 7728.1293 | 7603.164 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.46 |  | 0.45 |  | 0.45 | 0.47 | 0.47 | 0.46 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.7 | 19.6 |  | 19.2 |  | 19.3 | 20.3 | 20.2 | 19.2 | 20.1
| LIQUID LEVEL | mm | mm | 225.4 | 192 |  | 127 |  | 204.5 | 208.2 | 199.1 | 163.2 | 151.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.52 | 5.35 |  | 5.15 |  | 5.56 | 4.85 | 5.18 | 5.34 | 5.13
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 8
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 71.9 | 81.6 | 74.8 | 73.2 | 74.6 | 73.7 | 70.8 |  | 75.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 | 0 | 0 | 0 | 0 | 0.1 | 0.1 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.9 | 77.4 | 69.9 | 69.4 | 69.4 | 70.4 | 67.4 |  | 71.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.5 | 70.7 | 69 | 63.2 | 63.9 | 65.7 | 65.5 |  | 72.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 61.9 | 52 | 50.7 | 39.3 | 37.1 | 31.2 | 28.7 |  | 49.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 118 | 117.9 | 116.4 | 115.2 | 118 | 117.2 | 114.1 |  | 118.9
| INPUT | Kw | 1194kW |  | 1151 | 1210 | 1176 | 1184 | 1210 | 1195 | 1168 |  | 1214
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46630.5 | 47523.9 | 47515.4 | 45120 | 45112.2 | 47427 | 47419.1 |  | 46740.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 | 59.3 | 59.2 | 57.6 | 58 | 57.3 | 57.5 |  | 58.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.49 | 0.5 | 0.59 | 0.57 | 0.52 | 0.52 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 | 44.9 | 45 | 44.7 | 44.6 | 44.7 | 45 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.22 | 0.22 | 0.23 | 0.23 | 0.23 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.1 | 3.4 | 3.9 | 4.2 | 4.5 | 4.1 | 3.9 |  | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 | 2.3 | 3.1 | 3.7 | 3.6 | 3.7 | 2.8 |  | 3.3
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 2.2 | 1.8 | 1 | 0.7 | 1.1 | 1.3 | 0 | 1.2 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 684.1 | 675.36 | 664.8 | 679.04 | 636.9 | 743.6 | 643.7 |  | 656.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.5 | 12.6 | 13.5 | 13.2 | 13.4 | 12.8 | 12.7 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 | 4.5 | 4.9 | 4.7 | 4.3 | 4.8 | 4.1 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.8 | 8.1 | 8.6 | 8.5 | 9.1 | 8 | 8.6 | 0 | 9.1 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6951.5935 | 6316.8776 | 6601.94 | 6664.9423 | 6692.5982 | 6869.2841 | 6392.4018 | 0 | 6899.6074 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.87 | 0.85 | 0.86 | 0.84 | 0.87 | 0.83 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.1 | 36.9 | 36.7 | 36.2 | 36.5 | 36.8 | 36.8 |  | 36.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.7 | 38.4 | 37.7 | 37.8 | 37.2 | 38.2 | 37.1 |  | 36.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.6 | 4.6 | 4.2 | 3.5 | 2.9 | 4.3 | 3.4 | 0 | 2.4 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.8 | 28.8 | 28.5 | 29 | 28.7 | 28.7 | 28.5 |  | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.1 | 33.8 | 33.5 | 34.3 | 34.3 | 33.9 | 33.7 |  | 34.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 5 | 5 | 5.3 | 5.6 | 5.2 | 5.2 | 0 | 6 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1300.9 | 1300.88 | 1299.2 | 1297.24 | 1296.7 | 1271.34 | 1287.9 |  | 1146.1
| HEAT CAPACITY | kW | 8226.9 | 0 | 7961.6282 | 7510.8545 | 7501.1547 | 7939.2286 | 8385.127 | 7633.9122 | 7733.3487 | 0 | 7940.6467 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.46 | 0.47 | 0.46 | 0.46 | 0.47 | 0.47 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 | 19.7 | 20 | 19.5 | 19.7 | 20 | 19.9 |  | 19.6
| LIQUID LEVEL | mm | mm |  | 211.4 | 130.4 | 122.8 | 208 | 207 | 213.6 | 206.5 |  | 160.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.65 | 5.5 | 5.23 | 5.7 | 5.59 | 5.49 | 5.44 |  | 5.53
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 9
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 69.3 | 71.1 |  | 81.6 | 73.1 | 73.2 |  | 72.4 | 74.6 | 76.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% | 65.7 | 65.6 |  | 77.4 | 69.4 | 69.4 |  | 68.7 | 71 | 71.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 66 | 66.8 |  | 67.9 | 63.3 | 63.2 |  | 64.2 | 72 | 72.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 71.7 | 71.5 |  | 50.9 | 38 | 35.9 |  | 29.3 | 50.7 | 51.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 115.8 | 118.9 |  | 119.9 | 116.7 | 118 |  | 115.9 | 117 | 120.6
| INPUT | Kw | 1194kW | 1134 | 1162 |  | 1214 | 1200 | 1196 |  | 1181 | 1197 | 1227
COMPRESSOR | RUNNING TIME | Hr | NA | 46649.1 | 46641 |  | 47540.4 | 45145.2 | 45137.2 |  | 47444.1 | 46759 | 46750.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.4 |  | 59.3 | 57.7 | 57.9 |  | 57.4 | 45 | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.52 | 0.49 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.7 | 44.5 |  | 45.1 | 44.9 | 45.1 |  | 45.2 | 45 | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 | 0.23 | 0.23 |  | 0.22 | 0.22 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4 | 4.6 |  | 3.3 | 4.5 | 4.2 |  | 3.8 | 4.3 | 4.5
| SATURATION TEMPERATURE | CELCIUS | C | 3.7 | 4 |  | 2.6 | 3.6 | 3.6 |  | 2.7 | 3.3 | 3.1
| APPROACH TEMP | CELCIUS | C | 0.8 | 1.1 | 0 | 2.6 | 1.2 | 0.7 | 0 | 1.4 | 0.8 | 1.7 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 693.6 | 680.8 |  | 665.3 | 680.08 | 644.27 |  | 658.1 | 661.36 | 660.7
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.7 | 13.6 |  | 13.6 | 13.3 | 13.2 |  | 12.8 | 12.7 | 13.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.5 | 5.1 |  | 5.2 | 4.8 | 4.3 |  | 4.1 | 4.1 | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.2 | 8.5 | 0 | 8.4 | 8.5 | 8.9 | 0 | 8.7 | 8.6 | 8.9 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 6567.5751 | 6682.2171 | 0 | 6453.2564 | 6675.1501 | 6621.2506 | 0 | 6611.3972 | 6567.7783 | 6790.1039 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.84 |  | 0.87 | 0.84 | 0.85 |  | 0.85 | 0.82 | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.9 | 36.8 |  | 37.4 | 36.4 | 36.9 |  | 37.2 | 36.3 | 37
| SATURATED TEMEPRATURE | CELCIUS | C | 36.5 | 37.3 |  | 38.8 | 37.1 | 37.6 |  | 37.7 | 36.6 | 37.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 3.2 | 2.6 | 0 | 4.8 | 3.5 | 2.8 | 0 | 3.5 | 3.2 | 2.3 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.2 | 29.3 |  | 29.2 | 28 | 29.3 |  | 29.2 | 28 | 29.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.3 | 34.7 |  | 34 | 33.6 | 34.8 |  | 34.2 | 33.4 | 35.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.1 | 5.4 | 0 | 4.8 | 5.6 | 5.5 | 0 | 5 | 5.4 | 6 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1291.08 | 1286.6 |  | 1311.5 | 1291.64 | 1304.4 |  | 1299.2 | 1183.42 | 1140.6
| HEAT CAPACITY | kW | 8226.9 | 7603.358 | 8022.679 | 0 | 7269.2841 | 8352.4065 | 8284.2956 | 0 | 7501.1547 | 7379.2933 | 7902.5404 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.48 |  | 0.46 | 0.46 | 0.47 |  | 0.47 | 0.46 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 20 | 20.5 |  | 19.8 | 19.5 | 20.2 |  | 20.3 | 19.6 | 20.1
| LIQUID LEVEL | mm | mm | 219.5 | 216.1 |  | 122.1 | 204.4 | 216.4 |  | 212.8 | 161.9 | 152.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.49 | 5.42 |  | 5.29 | 5.41 | 5.59 |  | 5.49 | 5.4 | 5.44
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 10
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 69.1 | 76.7 | 76.7 |  | 74.3 | 74.3 | 74.3 | 74.6 | 74.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.7 | 72.3 | 72.4 |  | 69.2 | 69.6 | 69.6 | 71 | 71.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.3 | 66.6 | 68.8 |  | 63.8 | 64.8 | 65 | 71.1 | 71.8
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 64.3 | 50.1 | 51.8 |  | 38.1 | 34.9 | 30.9 | 53.1 | 51.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 115.6 | 115.1 | 116.4 |  | 117.2 | 118.1 | 117.3 | 119.1 | 118.7
| INPUT | Kw | 1194kW |  | 1147 | 1175 | 1186 |  | 1208 | 1186 | 1191 | 1194 | 1207
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46664.5 | 47557.9 | 47549.5 |  | 45160.6 | 47461 | 47453.4 | 46782 | 46774.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 | 59 | 59.1 |  | 57.9 | 57.2 | 57.5 | 58.6 | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.49 | 0.49 |  | 0.59 | 0.52 | 0.52 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 | 45 | 45 |  | 44.9 | 45.1 | 45 | 45 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.22 | 0.22 |  | 0.23 | 0.22 | 0.22 | 0.22 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 | 3.6 | 3.6 |  | 4.4 | 4 | 3.9 | 4.1 | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 | 2.6 | 2.8 |  | 3.6 | 2.9 | 2.9 | 3.6 | 3.2
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 2 | 2.1 | 0 | 0.6 | 1.1 | 1.2 | 0.6 | 1.3 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 683 | 674.24 | 662.9 |  | 648.2 | 640.2 | 656.3 | 662.88 | 650.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.3 | 12.6 | 13.4 |  | 13.2 | 13 | 12.9 | 12.8 | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 | 4.6 | 4.9 |  | 4.2 | 4 | 4.1 | 4.2 | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.5 | 8 | 8.5 | 0 | 9 | 9 | 8.8 | 8.6 | 8.9 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6703.8106 | 6228.545 | 6506.5242 | 0 | 6736.4896 | 6653.3487 | 6669.0993 | 6582.873 | 6684.2494 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.85 | 0.86 |  | 0.84 | 0.83 | 0.84 | 0.81 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.4 | 36.8 | 37 |  | 36.6 | 36.6 | 37 | 35.9 | 36.7
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.8 | 37.6 | 37.9 |  | 37.4 | 37 | 37.5 | 36.3 | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.5 | 4.3 | 4.2 | 0 | 2.9 | 3.5 | 3.5 | 2.4 | 2.2 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.9 | 28.5 | 28.8 |  | 28.9 | 28.4 | 28.8 | 28.2 | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.3 | 33.3 | 33.7 |  | 34.5 | 33.5 | 34 | 33.9 | 34.8
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.4 | 4.8 | 4.9 | 0 | 5.6 | 5.1 | 5.2 | 5.7 | 6.1 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1300.4 | 1298.92 | 1299.3 |  | 1291.2 | 1297.5 | 1291.4 | 1195.7 | 1136.7
| HEAT CAPACITY | kW | 8226.9 | 0 | 8108.7298 | 7199.5566 | 7351.6975 | 0 | 8349.5612 | 7641.1663 | 7754.3649 | 7870.0808 | 8006.7783 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.46 | 0.47 |  | 0.46 | 0.47 | 0.47 | 0.45 | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 | 19.6 | 20 |  | 19.6 | 19.8 | 20.1 | 36.3 | 19.7
| LIQUID LEVEL | mm | mm |  | 224.1 | 126.4 | 123.9 |  | 208.8 | 206.5 | 205.6 | 156.3 | 157.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.59 | 5.29 | 5.22 |  | 5.51 | 5.61 | 5.42 | 5.5 | 5.42
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 11
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 72.1 | 72.1 |  | 80.5 | 73.5 | 72.1 |  | 73.1 | 74.2 | 74.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.4 | 0.4 |  | 0 | 0 | 0 |  | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% | 65.8 | 65.8 |  | 76.7 | 68.8 | 66.3 |  | 69.5 | 68.6 | 68.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.2 | 68 |  | 69 | 64.2 | 63.7 |  | 65 | 75.1 | 73.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 49.1 | 58.2 |  | 47.9 | 41.3 | 38.2 |  | 33.2 | 50.9 | 47.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 118 | 119.1 |  | 119.5 | 116.5 | 116.2 |  | 116.7 | 118.1 | 118.5
| INPUT | Kw | 1194kW | 1154 | 1165 |  | 1205 | 1173 | 1175 |  | 1185 | 1189 | 1205
COMPRESSOR | RUNNING TIME | Hr | NA | 46682.2 | 46674.2 |  | 47573.6 | 45178.5 | 45170.5 |  | 474777.5 | 46804 | 46796
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 58.8 |  | 59.3 | 57.5 | 57.6 |  | 57.5 | 58.6 | 58.8
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.52 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 44.8 |  | 45 | 44.8 | 44.8 |  | 45 | 44.8 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.22 | 0.22 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.6 | 4.4 |  | 3.4 | 4.1 | 4.4 |  | 3.8 | 4.4 | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 4.1 | 3.9 |  | 2.5 | 3.3 | 3.6 |  | 2.7 | 3.5 | 3.5
| APPROACH TEMP | CELCIUS | C | 0.8 | 1.1 | 0 | 2.5 | 0.7 | 0.7 | 0 | 1.3 | 1.1 | 1.2 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 656.2 | 680.9 |  | 661.2 | 638.56 | 633.5 |  | 642.3 | 649.1 | 649.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 14.2 | 13.4 |  | 13.6 | 13.1 | 13.3 |  | 12.8 | 14.1 | 13.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.9 | 5 |  | 5 | 4 | 4.3 |  | 4 | 4.6 | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 9.3 | 8.4 | 0 | 8.6 | 9.1 | 9 | 0 | 8.8 | 9.5 | 9 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 7046.9515 | 6604.5727 | 0 | 6566.1894 | 6710.0416 | 6583.7182 | 0 | 6526.836 | 7120.612 | 6748.9607 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.83 |  | 0.86 | 0.82 | 0.84 |  | 0.85 | 0.81 | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.7 | 36.6 |  | 37.3 | 35.8 | 36.7 |  | 37.1 | 35.7 | 36.9
| SATURATED TEMEPRATURE | CELCIUS | C | 36.8 | 37.1 |  | 38.2 | 36.6 | 37.4 |  | 37.5 | 36.2 | 37.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 3.2 | 2.5 | 0 | 4.3 | 2.9 | 2.8 | 0 | 3.4 | 2.5 | 2.3 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.2 | 29 |  | 29 | 28.2 | 29.1 |  | 29 | 28 | 28.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.6 | 34.6 |  | 33.9 | 33.7 | 34.6 |  | 34.1 | 33.7 | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.4 | 5.6 | 0 | 4.9 | 5.5 | 5.5 | 0 | 5.1 | 5.7 | 6 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1298.1 | 1296.4 |  | 1306.6 | 1286.9 | 1300.4 |  | 1298 | 1140 | 1137.8
| HEAT CAPACITY | kW | 8226.9 | 8094.388 | 8383.1871 | 0 | 7393.0023 | 8173.1524 | 8258.8915 | 0 | 7644.1109 | 7503.4642 | 7883.1409 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.48 |  | 0.46 | 0.46 | 0.47 |  | 0.47 | 0.46 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.7 | 20.5 |  | 19.8 | 19.4 | 20.2 |  | 20 | 19.4 | 20.2
| LIQUID LEVEL | mm | mm | 171.1 | 210.6 |  | 123.8 | 199.2 | 208.2 |  | 211.2 | 165.3 | 164.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.97 | 5.36 |  | 5.36 | 5.73 | 5.67 |  | 5.42 | 5.9 | 5.52
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 12
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 71.2 | 83.8 | 77.7 |  | 70.4 | 73.8 | 73.3 | 75.6 | 74.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 | 0 | 0 |  | 0 | 0.2 | 0 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.2 | 80.3 | 72.8 |  | 66.1 | 70.2 | 70.6 | 70.5 | 69.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 64.7 | 67.3 | 67.2 |  | 63.6 | 65.7 | 63.5 | 72.1 | 68.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 56 | 53.1 | 51.3 |  | 38.7 | 34.5 | 30.9 | 56.6 | 50.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 116.6 | 117.5 | 117.7 |  | 116.4 | 116.2 | 118 | 116.9 | 116.9
| INPUT | Kw | 1194kW |  | 1132 | 1201 | 1186 |  | 1176 | 1167 | 1194 | 1179 | 1185
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46697.2 | 47591.3 | 47599.8 |  | 45193.5 | 47495.5 | 47504 | 46825.5 | 46834
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 | 58.9 | 59.3 |  | 57.7 | 57.3 | 57.3 | 58.3 | 58.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.48 | 0.49 |  | 0.59 | 0.52 | 0.52 | 0.47 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 | 45.1 | 44.8 |  | 45.1 | 45.1 | 45 | 45.1 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.22 |  | 0.23 | 0.22 | 0.22 | 0.22 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 | 3 | 3.6 |  | 4.3 | 3.5 | 4.1 | 4.1 | 3.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.7 | 2 | 2.7 |  | 3.6 | 2.7 | 2.9 | 2.9 | 2.7
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 2.4 | 2.3 | 0 | 0.7 | 1.2 | 1.3 | 1.2 | 1.2 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 669.2 | 669.3 | 650.3 |  | 648.9 | 651.8 | 653.5 | 661.9 | 638.1
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.4 | 13.2 | 13.3 |  | 13.1 | 12.8 | 12.9 | 13.1 | 12.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 | 4.4 | 5 |  | 4.3 | 3.9 | 4.2 | 4.1 | 3.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.7 | 8.8 | 8.3 | 0 | 8.8 | 8.9 | 8.7 | 9 | 8.9 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6722.9099 | 6801.2009 | 6232.6674 | 0 | 6593.903 | 6698.6374 | 6565.1848 | 6878.8684 | 6557.8406 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.83 | 0.86 |  | 0.84 | 0.84 | 0.85 | 0.8 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.4 | 36 | 37.1 |  | 36.6 | 35.5 | 37.2 | 34.9 | 36.7
| SATURATED TEMEPRATURE | CELCIUS | C |  | 37 | 36.9 | 38 |  | 37.3 | 36 | 37.6 | 35.4 | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.6 | 4.6 | 4.1 | 0 | 2.8 | 3.5 | 3.5 | 2.5 | 2.2 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.1 | 27.4 | 28.8 |  | 29 | 27.3 | 28.9 | 27.2 | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.4 | 32.3 | 33.9 |  | 34.5 | 32.5 | 34.1 | 32.9 | 34.8
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 4.9 | 5.1 | 0 | 5.5 | 5.2 | 5.2 | 5.7 | 6 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1297.3 | 1312.7 | 1300.9 |  | 1303.2 | 1305.7 | 1289.9 | 1202.7 | 1110
| HEAT CAPACITY | kW | 8226.9 | 0 | 7939.5958 | 7427.5173 | 7661.1894 | 0 | 8276.6744 | 7840.2309 | 7745.358 | 7916.1547 | 7690.5312 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.44 | 0.47 |  | 0.46 | 0.45 | 0.47 | 0.44 | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 | 18.7 | 19.9 |  | 19.8 | 19.2 | 20.1 | 18.6 | 19.6
| LIQUID LEVEL | mm | mm |  | 229.9 | 116.5 | 120.8 |  | 207.3 | 208.6 | 203.6 | 168 | 159.4
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.74 | 5.4 | 5.18 |  | 5.52 | 5.67 | 5.39 | 5.59 | 5.54
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 13
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 72 | 72 |  | 75.3 | 73.3 | 70.8 |  | 73.5 | 75.1 | 73.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% | 65.8 | 65.8 |  | 70.3 | 68.4 | 67.8 |  | 68.7 | 70.7 | 68.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69 | 66.7 |  | 68.7 | 63.9 | 62.8 |  | 65.4 | 73.8 | 72.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 51.1 | 69.1 |  | 51.1 | 41.7 | 36.8 |  | 30.6 | 32.8 | 48.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 115.2 | 117.5 |  | 116.7 | 114.1 | 115.8 |  | 115.5 | 116.6 | 117.2
| INPUT | Kw | 1194kW | 1138 | 1153 |  | 1177 | 1168 | 1172 |  | 1177 | 1188 | 1196
COMPRESSOR | RUNNING TIME | Hr | NA | 46710.6 | 46701.7 |  | 47603.5 | 45208.2 | 45199.2 |  | 47510.4 | 46843.6 | 46834.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.8 | 58.8 |  | 58.9 | 57.3 | 57.7 |  | 57.6 | 58.5 | 58.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.52 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 44.6 |  | 45.2 | 45.1 | 45 |  | 44.9 | 45 | 45.2
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.22 | 0.22 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.2 | 4.2 |  | 3.8 | 4.1 | 4.2 |  | 3.9 | 4.3 | 4.3
| SATURATION TEMPERATURE | CELCIUS | C | 3.7 | 3.8 |  | 3 | 3.4 | 3.6 |  | 2.8 | 3.3 | 3.3
| APPROACH TEMP | CELCIUS | C | 1.2 | 1.1 | 0 | 1.8 | 0.6 | 0.7 | 0 | 1.2 | 1.1 | 1.2 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 691.5 | 686 |  | 670.5 | 655.2 | 651.1 |  | 653.8 | 664.5 | 658.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.3 | 13.3 |  | 13.5 | 12.9 | 13.3 |  | 12.8 | 13.3 | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.9 | 4.9 |  | 4.8 | 4 | 4.3 |  | 4 | 4.4 | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.4 | 8.4 | 0 | 8.7 | 8.9 | 9 | 0 | 8.8 | 8.9 | 9 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 6707.3903 | 6654.0416 | 0 | 6735.97 | 6733.5797 | 6766.6282 | 0 | 6643.6952 | 6829.157 | 6844.5727 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.82 |  | 0.84 | 81 | 0.84 |  | 0.84 | 0.81 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.2 | 36 |  | 36.4 | 35.4 | 36.5 |  | 36.9 | 35.3 | 36.6
| SATURATED TEMEPRATURE | CELCIUS | C | 35.7 | 36.4 |  | 37.4 | 36.1 | 37.2 |  | 37.4 | 35.7 | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.6 | 2.5 | 0 | 4.3 | 3 | 2.8 | 0 | 3.5 | 2.5 | 2.3 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.4 | 28.3 |  | 28.3 | 27.6 | 28.9 |  | 28.8 | 27.4 | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.1 | 33.9 |  | 33.1 | 33.1 | 34.4 |  | 33.9 | 33.2 | 34.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.7 | 5.6 | 0 | 4.8 | 5.5 | 5.5 | 0 | 5.1 | 5.8 | 6 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1293.2 | 1293.5 |  | 1303.1 | 1301.9 | 1298.3 |  | 1299.6 | 1188.8 | 1146.9
| HEAT CAPACITY | kW | 8226.9 | 8511.8245 | 8364.4342 | 0 | 7222.7252 | 8268.418 | 8245.5543 | 0 | 7653.5335 | 7961.94 | 7946.1894 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.47 |  | 0.47 | 0.45 | 0.46 |  | 0.47 | 0.45 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.5 | 20 |  | 19.7 |  | 19.3 |  | 20.1 | 18.9 | 19.9
| LIQUID LEVEL | mm | mm | 214.2 | 223.7 |  | 131.6 | 194.7 | 203.9 |  | 207.3 | 156.9 | 169.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.65 | 5.43 |  | 5.3 | 5.67 | 5.52 |  | 5.53 | 5.49 | 5.46
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 14
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 72.6 |  | 74.6 |  | 72.5 |  | 74.8 |  | 75
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 |  | 0 |  | 0 |  | 0.2 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.9 |  | 69 |  | 68.4 |  | 69.6 |  | 70.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 68.1 |  | 69.9 |  | 63.9 |  | 65.5 |  | 74.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 70.1 |  | 49.6 |  | 37.1 |  | 69.6 |  | 49.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 119.4 |  | 116.9 |  | 117.4 |  | 116.5 |  | 120.3
| INPUT | Kw | 1194kW |  | 1169 |  | 1177 |  | 1189 |  | 1183 |  | 1221
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46720 |  | 47613 |  | 45223 |  | 47520 |  | 46858
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 |  | 59.2 |  | 57.9 |  | 57.5 |  | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 |  | 0.59 |  | 0.52 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.6 |  | 45.2 |  | 45.1 |  | 44.9 |  | 44.6
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.24 |  | 0.23 |  | 0.23 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 4.1 |  | 4.5 |  | 3.8 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.1 |  | 3.1 |  | 3.4 |  | 2.7 |  | 3.4
| APPROACH TEMP | CELCIUS | C | 0 | 0.6 | 0 | 1.9 | 0 | 1.1 | 0 | 1.1 | 0 | 1.1 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 679.84 |  | 660.24 |  | 628.64 |  | 652.56 |  | 652.72
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.1 |  | 13.2 |  | 13.5 |  | 12.8 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 |  | 5 |  | 4.5 |  | 3.8 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.4 | 0 | 8.2 | 0 | 9 | 0 | 9 | 0 | 8.7 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6594.291 | 0 | 6251.6952 | 0 | 6533.2102 | 0 | 6781.8014 | 0 | 6557.3487 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.86 |  | 0.84 |  | 0.84 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.6 |  | 37 |  | 36.6 |  | 37 |  | 36.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.9 |  | 37.8 |  | 37.1 |  | 37.4 |  | 36.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 3.4 | 0 | 4.7 | 0 | 3.6 | 0 | 4.2 | 0 | 3 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.3 |  | 28.1 |  | 28.2 |  | 28.1 |  | 28.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.5 |  | 33.1 |  | 33.5 |  | 33.2 |  | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 0 | 5 | 0 | 5.3 | 0 | 5.1 | 0 | 5.7 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1300.6 |  | 1297.24 |  | 1293.88 |  | 1294.44 |  | 1142.82
| HEAT CAPACITY | kW | 8226.9 | 0 | 7809.6074 | 0 | 7489.8383 | 0 | 7918.6651 | 0 | 7623.1455 | 0 | 7522.0254 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 |  | 0.47 |  | 0.46 |  | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 |  | 20.4 |  | 19.3 |  | 20 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 245.9 |  | 127.9 |  | 208.2 |  | 208.6 |  | 161.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.4 |  | 5.36 |  | 5.54 |  | 5.5 |  | 5.45
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 15
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 72.6 | 80 | 74.1 | 72.7 | 73.3 | 75.1 | 73.9 |  | 73.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 67 | 75.5 | 69.1 | 67.8 | 67.8 | 70 | 69.6 |  | 67.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.5 | 64.5 | 69.7 | 61.4 | 64.4 | 62.7 | 65.7 |  | 74.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 58.5 | 49.2 | 53.7 | 39.5 | 40.2 | 34.5 | 31.7 |  | 49.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 119 | 116.5 | 115.8 | 115.8 | 116.3 | 119.2 | 115.9 |  | 117
| INPUT | Kw | 1194kW |  | 1164 | 1182 | 1169 | 1180 | 1178 | 1208 | 1178 |  | 1189
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46744.8 | 47643 | 47633 | 45243.4 | 45233.4 | 47554.6 | 47544.6 |  | 46868.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.3 | 59.2 | 59.2 | 57.8 | 57.7 | 57.4 | 57.3 |  | 44.8
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.49 | 0.49 | 0.59 | 0.59 | 0.53 | 0.52 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 | 44.8 | 44.9 | 45 | 44.9 | 45.1 | 45 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.22 | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.2
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.8 | 3 | 4.1 | 4.3 | 4.3 | 4.4 | 3.8 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.2 | 2.1 | 3.1 | 3.4 | 3.5 | 3.4 | 2.7 |  | 3.4
| APPROACH TEMP | CELCIUS | C | 0 | 0.3 | 2.4 | 1.7 | 0.7 | 1.1 | 1.3 | 1.2 | 0 | 1 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 670.24 | 675.8 | 656.64 | 680.8 | 647.52 | 745.5 | 645.84 |  | 649.44
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.1 | 12.5 | 13.2 | 12.6 | 13.5 | 12.7 | 13.1 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.5 | 4.5 | 4.8 | 4.1 | 4.6 | 4.7 | 3.9 |  | 4.4
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.6 | 8 | 8.4 | 8.5 | 8.9 | 8 | 9.2 | 0 | 8.8 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6655.963 | 6242.9561 | 6369.2564 | 6682.2171 | 6654.6513 | 6886.836 | 6861.1178 | 0 | 6599.3903 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.84 | 0.84 | 0.83 | 0.83 | 0.84 | 0.83 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.8 | 36.7 | 36.5 | 36.2 | 36 | 36.9 | 36.4 |  | 36
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.3 | 37.5 | 37.3 | 36.9 | 36.7 | 37.4 | 36.9 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 3.3 | 4.3 | 4.8 | 2.9 | 3.7 | 3.6 | 4.4 | 0 | 3.1 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.9 | 28.3 | 27.5 | 28.5 | 27.6 | 28.5 | 27.5 |  | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33 | 33.2 | 32.5 | 34 | 33 | 33.8 | 32.5 |  | 33.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 4.9 | 5 | 5.5 | 5.4 | 5.3 | 5 | 0 | 5.7 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1297.52 | 1295.7 | 1304.38 | 1298.8 | 1287.16 | 1266 | 1299.9 |  | 1139.04
| HEAT CAPACITY | kW | 8226.9 | 0 | 7641.2841 | 7331.3279 | 7531.0624 | 8248.7298 | 8026.1709 | 7748.037 | 7505.1963 | 0 | 7497.1455 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.45 | 0.47 | 0.46 | 0.46 | 0.47 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.5 | 19.2 | 19.7 | 19.5 | 19.8 | 20.3 | 19.7 |  | 19.7
| LIQUID LEVEL | mm | mm |  | 144.3 | 117.8 | 130.4 | 205.2 | 208.3 | 215.7 | 208.1 |  | 163.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.56 | 5.18 | 5.33 | 5.29 | 5.69 | 4.86 | 5.64 |  | 5.55
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 16
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 69.9 | 69.9 |  | 74.6 |  | 71.3 | 73.7 | 73.5 | 69.8 | 74.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.8 | 0.8 |  | 0 |  | 0 | 0.1 | 0.2 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% | 64.1 | 64.1 |  | 69.3 |  | 68.4 | 70 | 68.7 | 65.9 | 68.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 62 | 68 |  | 69.4 |  | 63 | 62.7 | 65 | 67.9 | 73.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 68.8 | 59 |  | 54.8 |  | 39.3 | 35 | 33.9 | 43.1 | 52.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 113.4 | 117.6 |  | 117 |  | 116.4 | 118 | 115.6 | 112.7 | 118.7
| INPUT | Kw | 1194kW | 1109 | 1147 |  | 1181 |  | 1186 | 1196 | 1176 | 1144 | 1205
COMPRESSOR | RUNNING TIME | Hr | NA | 46764 | 46754 |  | 47655 |  | 45257 | 47578 | 47568 | 46888 | 46878
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 58.1 |  | 59 |  | 57.8 | 57.3 | 57.4 | 58.5 | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.5 |  | 0.59 | 0.52 | 0.52 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.2 | 45.1 |  | 44.7 |  | 44.9 | 45 | 45 | 45.1 | 45.6
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.24 | 0.23 | 0.22 | 0.22 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.4 | 4.7 |  | 4.2 |  | 4.2 | 4.1 | 3.8 | 3.7 | 4.5
| SATURATION TEMPERATURE | CELCIUS | C | 3.5 | 4.2 |  | 3.2 |  | 3.4 | 3.3 | 3.7 | 2.8 | 3.5
| APPROACH TEMP | CELCIUS | C | 0.7 | 0.6 | 0 | 1.8 | 0 | 1.3 | 1.3 | 0.2 | 1.1 | 1.1 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 695.2 | 682 |  | 663.4 |  | 635.6 | 747.52 | 637.6 | 666.96 | 654.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.2 | 13.2 |  | 13.4 |  | 13.7 | 12.5 | 13.1 | 12.1 | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.2 | 4.8 |  | 5 |  | 4.7 | 4.6 | 3.9 | 3.9 | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8 | 8.4 | 0 | 8.4 | 0 | 9 | 7.9 | 9.2 | 8.2 | 8.7 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 6422.1709 | 6615.2425 | 0 | 6434.8268 | 0 | 6605.5427 | 6819.1778 | 6773.5797 | 6315.3256 | 6579.2494 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.83 |  | 0.85 |  | 0.83 | 0.84 | 0.84 | 0.81 | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.4 | 36.2 |  | 37 |  | 36.4 | 36.5 | 36.9 | 35.5 | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C | 36.3 | 36.8 |  | 37.8 |  | 37.1 | 37.3 | 37.3 | 36.2 | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 3.3 | 2.7 | 0 | 4.3 | 0 | 2.9 | 4.4 | 3.6 | 3.2 | 2.4 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.9 | 28.8 |  | 28.6 |  | 28.5 | 27.8 | 28.8 | 27.8 | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33 | 34.1 |  | 33.5 |  | 34.2 | 32.9 | 33.7 | 33 | 34.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.1 | 5.3 | 0 | 4.9 | 0 | 5.7 | 5.1 | 4.9 | 5.2 | 6 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1297.1 | 1293.1 |  | 1307.8 |  | 1302.1 | 1290.94 | 1296.8 | 1201.06 | 1140.7
| HEAT CAPACITY | kW | 8226.9 | 7638.8106 | 7913.8915 | 0 | 7399.7921 | 0 | 8570.4042 | 7602.5335 | 7337.552 | 7211.9076 | 7903.2333 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.47 |  | 0.47 |  | 0.46 | 0.47 | 0.47 | 0.45 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.3 | 20.1 |  | 20.1 |  | 19.4 | 19.8 | 20 | 19.6 | 20.1
| LIQUID LEVEL | mm | mm | 213.1 | 175.9 |  | 119.1 |  | 203.4 | 214.3 | 202.8 | 156.2 | 167.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.59 | 5.68 |  | 5.34 |  | 5.54 | 4.77 | 5.69 | 5.45 | 5.52
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 17
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 69.9 | 76.4 | 74.6 | 69.2 | 72.5 | 71.8 | 71.2 |  | 75
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.8 | 0 | 0 | 0 | 0 | 0.1 | 0.2 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.1 | 71.7 | 69 | 65.5 | 68.4 | 69.1 | 67.3 |  | 70.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 65.3 | 66 | 69.9 | 62.7 | 63.9 | 64.4 | 65.1 |  | 74.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 74.7 | 49 | 49.6 | 37.2 | 37.1 | 33.7 | 33 |  | 49.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.3 | 115 | 116.9 | 114.9 | 117.4 | 116.9 | 114.3 |  | 120.3
| INPUT | Kw | 1194kW |  | 1136 | 1163 | 1177 | 1158 | 1189 | 1188 | 1164 |  | 1221
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46776.8 | 47674.5 | 47664 | 45276.2 | 45265.8 | 47604.8 | 47590.9 |  | 46900.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.8 | 59 | 59.2 | 57.4 | 57.9 | 57.4 | 57.5 |  | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.49 | 0.5 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.5
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 | 45.1 | 45.2 | 45 | 45.1 | 44 | 44.9 |  | 44.6
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.23 | 0.23 | 0.23 | 0.23 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.2 | 3.3 | 4.1 | 4.2 | 4.5 | 4.2 | 4 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.7 | 2.4 | 3.1 | 3.4 | 3.4 | 3.2 | 2.7 |  | 3.4
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 2.2 | 1.9 | 1.4 | 1.1 | 1.3 | 1.5 | 0 | 1.1 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 697.5 | 674.56 | 660.24 | 679.92 | 628.64 | 719.92 | 647.1 |  | 652.72
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.1 | 12.5 | 13.2 | 13.2 | 13.5 | 12.8 | 12.9 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 | 4.6 | 5 | 4.8 | 4.5 | 4.5 | 4.2 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.4 | 7.9 | 8.2 | 8.4 | 9 | 8.3 | 8.7 | 0 | 8.7 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6765.5889 | 6153.6074 | 6251.6952 | 6595.067 | 6533.2102 | 6899.9261 | 6500.8891 | 0 | 6557.3487 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.85 | 0.86 | 0.84 | 0.84 | 0.85 | 0.81 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.6 | 36.7 | 37 | 36.3 | 36.6 | 37 | 37 |  | 36.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.9 | 37.6 | 37.8 | 37 | 37.1 | 37.5 | 37.4 |  | 36.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 3.4 | 4.6 | 4.7 | 3.4 | 3.6 | 4.3 | 3.4 | 0 | 3 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.3 | 28 | 28.1 | 28.2 | 28.2 | 27.9 | 28.9 |  | 28.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.5 | 33 | 33.1 | 33.6 | 33.5 | 33.2 | 34 |  | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 5 | 5 | 5.4 | 5.3 | 5.3 | 5.1 | 0 | 5.7 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1306.8 | 1299.34 | 1297.24 | 1297.94 | 1293.88 | 1272.32 | 1302.2 |  | 1142.82
| HEAT CAPACITY | kW | 8226.9 | 0 | 7846.836 | 7501.963 | 7489.8383 | 8093.3903 | 7918.6651 | 7786.7159 | 7668.8453 | 0 | 7522.0254 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 | 0.46 | 0.47 | 0.47 | 0.46 | 0.47 | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 | 19.6 | 20.4 | 19.9 | 19.3 | 20.2 | 20 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 245.9 | 126.4 | 127.9 | 206.4 | 208.2 | 214.5 | 208.6 |  | 161.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.4 | 5.25 | 5.36 | 5.35 | 5.54 | 5.14 | 5.42 |  | 5.45
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 18
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 68.3 | 71.3 |  | 78.4 | 74.1 | 71.1 |  | 72.3 | 72.8 | 74.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.1 |  | 0 | 0 | 0 |  | 0.2 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% | 64.3 | 66.2 |  | 76.2 | 69.6 | 67.2 |  | 69.2 | 68.6 | 68.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 68.8 | 77.2 |  | 66.9 | 62.8 | 63 |  | 65 | 75.8 | 70.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 56.1 | 65.4 |  | 50 | 36.8 | 38.2 |  | 30.7 | 52.3 | 48.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 116 | 116 |  | 116.4 | 116.4 | 115 |  | 116.6 | 117.7 | 116.6
| INPUT | Kw | 1194kW | 1134 | 1150 |  | 1187 | 1190 | 1186 |  | 1182 | 1191 | 1182
COMPRESSOR | RUNNING TIME | Hr | NA | 46796 | 46788.5 |  | 47689.7 | 45299.7 | 45291.5 |  | 47617 | 46920.8 | 46912.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.2 |  | 59.3 | 57.5 | 57.9 |  | 57.3 | 58.7 | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 |  | 0.49 | 0.59 | 0.59 |  | 0.52 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 44.7 |  | 44.8 | 45.1 | 45 |  | 44.9 | 45.1 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.25 | 0.23 |  | 0.21 | 0.23 | 0.23 |  | 0.22 | 0.23 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.3 | 4 |  | 3.1 | 4.3 | 4.5 |  | 3.9 | 4.6 | 4
| SATURATION TEMPERATURE | CELCIUS | C | 4 | 3.5 |  | 2.2 | 3.5 | 3.7 |  | 2.9 | 3.5 | 2.8
| APPROACH TEMP | CELCIUS | C | 0.5 | 0.9 | 0 | 2.4 | 0.8 | 0.6 | 0 | 1.2 | 0.8 | 1.2 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 652.4 | 682.7 |  | 666.6 | 641.9 | 671.6 |  | 645.9 | 635.9 | 636.2
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.1 | 12.8 |  | 12.9 | 13.2 | 12.9 |  | 13 | 13 | 12.9
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.5 | 4.4 |  | 4.6 | 4.3 | 4.3 |  | 4.1 | 4.3 | 4
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.6 | 8.4 | 0 | 8.3 | 8.9 | 8.6 | 0 | 8.9 | 8.7 | 8.9 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 6478.7991 | 6622.0323 | 0 | 6388.8915 | 6596.8938 | 6669.4688 | 0 | 6638.0023 | 6388.3718 | 6538.3141 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.82 |  | 0.85 | 0.84 | 0.83 |  | 0.84 | 0.82 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36 | 36.2 |  | 36.8 | 36.5 | 36.4 |  | 36.8 | 36.4 | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C | 36.6 | 36.6 |  | 37.7 | 37.2 | 37.1 |  | 37.3 | 36.7 | 36.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.5 | 2.5 | 0 | 4.2 | 2.9 | 2.9 | 0 | 3.6 | 2.4 | 2.3 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.8 | 28.6 |  | 28.5 | 28.9 | 28.7 |  | 28.7 | 28.6 | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.1 | 34.1 |  | 33.5 | 34.3 | 34.2 |  | 33.7 | 34.3 | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.3 | 5.5 | 0 | 5 | 5.4 | 5.5 | 0 | 5 | 5.7 | 5.9 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1295.4 | 1296.2 |  | 1297.2 | 1292.7 | 1302.3 |  | 1298.4 | 1191.9 | 1142.5
| HEAT CAPACITY | kW | 8226.9 | 7927.9677 | 8232.2171 | 0 | 7489.6074 | 8060.7159 | 8270.9584 | 0 | 7496.5358 | 7845.0693 | 7783.776 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.47 |  | 0.46 | 0.47 | 0.46 |  | 0.47 | 0.46 | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 20 | 20 |  | 19.2 | 19.9 | 19.7 |  | 20 | 19.8 | 19.5
| LIQUID LEVEL | mm | mm | 170.4 | 196.4 |  | 127.6 | 204.7 | 193.6 |  | 208.1 | 158.1 | 159.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.8 | 5.36 |  | 5.11 | 5.65 | 5.35 |  | 5.48 | 5.68 | 5.65
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 19
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 73.9 | 74.1 | 80.6 | 80.6 |  | 72.4 | 74.8 | 75.4 |  | 76.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.8 | 0.8 | 0 | 0 |  | 0 | 0.1 | 0.1 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 68.4 | 68.4 | 76.8 | 76.3 |  | 69.2 | 70.2 | 70.4 |  | 72.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 61.4 | 65.9 | 63.9 | 68.2 |  | 63.23 | 62.5 | 65.1 |  | 72
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 84.1 | 67.5 | 47.7 | 50.1 |  | 39.4 | 32.1 | 31.2 |  | 49.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 116.4 | 119.1 | 116.3 | 117.6 |  | 115.1 | 119.1 | 117.1 |  | 120.6
| INPUT | Kw | 1194kW | 1146 | 1182 | 1186 | 1207 |  | 1186 | 1203 | 1199 |  | 1230
COMPRESSOR | RUNNING TIME | Hr | NA | 46816.3 | 46807.1 | 47708.5 | 47699.3 |  | 45315.4 | 47635.9 | 47626.7 |  | 46936.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 58.8 | 59.1 | 59.2 |  | 57.9 | 57.3 | 57.5 |  | 58.8
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 | 0.49 | 0.49 |  | 0.59 | 0.52 | 0.52 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.2 | 45 | 45 | 45 |  | 44.9 | 45 | 44.8 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.23 | 0.21 | 0.22 |  | 0.23 | 0.22 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.7 | 4.7 | 3.1 | 3.4 |  | 4.3 | 4.4 | 4 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C | 3.1 | 4.2 | 2.1 | 2.6 |  | 3.5 | 3 | 2.8 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 1 | 0.6 | 2.2 | 2.2 | 0 | 0.7 | 1.6 | 1.3 | 0 | 1 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 692.7 | 680 | 673.6 | 662.9 |  | 648.2 | 749 | 637.5 |  | 685.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.4 | 13.4 | 12.3 | 13.5 |  | 13.2 | 12.4 | 13.1 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.1 | 4.8 | 4.3 | 4.8 |  | 4.2 | 4.6 | 4.1 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.3 | 8.6 | 8 | 8.7 | 0 | 9 | 7.8 | 9 | 0 | 8.7 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 6639.0416 | 6752.8868 | 6222.6328 | 6659.6189 | 0 | 6736.4896 | 6746.1894 | 6625.2887 | 0 | 6887.6674 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.83 | 0.82 | 0.85 | 0.85 |  | 0.83 | 0.85 | 0.81 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.5 | 36.2 | 37.1 | 36.9 |  | 36.2 | 37.4 | 36.9 |  | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C | 36.9 | 36.7 | 37.9 | 37.8 |  | 37.1 | 37.8 | 37.3 |  | 36.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.5 | 2.6 | 4.1 | 4.3 | 0 | 3 | 3.5 | 3.6 | 0 | 2.3 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.9 | 28.6 | 28.8 | 28.5 |  | 28.6 | 28 | 28.5 |  | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.4 | 34.1 | 33.8 | 33.5 |  | 34.1 | 34.3 | 33.7 |  | 34.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.5 | 5 | 5 | 0 | 5.5 | 6.3 | 5.2 | 0 | 6.2 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1243 | 1293.7 | 1270.2 | 1305.4 |  | 1299.8 | 1236.4 | 1295.3 |  | 1147.4
| HEAT CAPACITY | kW | 8226.9 | 7894.3418 | 8216.3395 | 7333.7182 | 7536.9515 | 0 | 8255.0808 | 8994.5958 | 7777.7829 | 0 | 8214.642 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.46 | 0.46 | 0.46 |  | 0.46 | 0.47 | 0.47 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.8 | 19.5 | 19.5 | 19.6 |  | 19.5 | 20.4 | 20.1 |  | 19.8
| LIQUID LEVEL | mm | mm | 210 | 121.7 | 122 | 127.7 |  | 206.8 | 206 | 208.2 |  | 154.4
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.38 | 5.34 | 4.99 | 5.41 |  | 5.59 | 4.81 | 5.6 |  | 5.31
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 20
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 62.8 | 71.1 |  | 81.6 | 61.7 | 73.2 |  | 72.4 | 66.2 | 76.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% | 55 | 65.6 |  | 77.4 | 54.4 | 69.4 |  | 68.7 | 60.3 | 71.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 60.7 | 66.8 |  | 67.9 | 59.4 | 63.2 |  | 64.2 | 66.7 | 72.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 76.5 | 71.5 |  | 50.9 | 38.6 | 35.9 |  | 29.3 | 48.1 | 51.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 104.4 | 118.9 |  | 119.9 | 104.8 | 118 |  | 115.9 | 108.5 | 120.6
| INPUT | Kw | 1194kW | 1027 | 1162 |  | 1214 | 1074 | 1196 |  | 1181 | 1101 | 1227
COMPRESSOR | RUNNING TIME | Hr | NA | 46842.1 | 46837.2 |  | 47540.4 | 45336.2 | 45329.2 |  | 47444.1 | 46957.1 | 46949.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.8 | 58.4 |  | 59.3 | 57.7 | 57.9 |  | 57.4 | 58.5 | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.51 | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.52 | 0.47 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 44.5 |  | 45.1 | 45.2 | 45.1 |  | 45.2 | 45 | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.22 | 0.22 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.1 | 4.6 |  | 3.3 | 4.2 | 4.2 |  | 3.8 | 3.9 | 4.5
| SATURATION TEMPERATURE | CELCIUS | C | 2.6 | 4 |  | 2.6 | 3.4 | 3.6 |  | 2.7 | 2.8 | 3.1
| APPROACH TEMP | CELCIUS | C | 1.8 | 1.1 | 0 | 2.6 | 0.7 | 0.7 | 0 | 1.4 | 1.2 | 1.7 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 689.9 | 680.8 |  | 665.3 | 680.8 | 644.27 |  | 658.1 | 686.3 | 660.7
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.1 | 13.6 |  | 13.6 | 12 | 13.2 |  | 12.8 | 12.1 | 13.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.4 | 5.1 |  | 5.2 | 4.1 | 4.3 |  | 4.1 | 4 | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.7 | 8.5 | 0 | 8.4 | 7.9 | 8.9 | 0 | 8.7 | 8.1 | 8.9 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 6134.2148 | 6682.2171 | 0 | 6453.2564 | 6210.5312 | 6621.2506 | 0 | 6611.3972 | 6419.2032 | 6790.1039 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.84 |  | 0.87 | 0.79 | 0.85 |  | 0.85 | 0.79 | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34 | 36.8 |  | 37.4 | 34.6 | 36.9 |  | 37.2 | 34.6 | 37
| SATURATED TEMEPRATURE | CELCIUS | C | 34.6 | 37.3 |  | 38.8 | 35.3 | 37.6 |  | 37.7 | 35 | 37.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  |  | 2.6 | 0 | 4.8 | 2.9 | 2.8 | 0 | 3.5 | 2.4 | 2.3 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.3 | 29.3 |  | 29.2 | 27.3 | 29.3 |  | 29.2 | 27.2 | 29.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 32.2 | 34.7 |  | 34 | 32.4 | 34.8 |  | 34.2 | 32.6 | 35.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 4.9 | 5.4 | 0 | 4.8 | 5.1 | 5.5 | 0 | 5 | 5.4 | 6 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1298.2 | 1286.6 |  | 1311.5 | 1290.6 | 1304.4 |  | 1299.2 | 1189 | 1140.6
| HEAT CAPACITY | kW | 8226.9 | 7345.4734 | 8022.679 | 0 | 7269.2841 | 7600.5312 | 8284.2956 | 0 | 7501.1547 | 7414.0878 | 7902.5404 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.48 |  | 0.46 | 0.45 | 0.47 |  | 0.47 | 0.45 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.1 | 20.5 |  | 19.8 | 19.1 | 20.2 |  | 20.3 | 18.9 | 20.1
| LIQUID LEVEL | mm | mm | 291.4 | 216.1 |  | 122.1 | 203.1 | 216.4 |  | 212.8 | 165.8 | 152.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.73 | 5.42 |  | 5.29 | 5.44 | 5.59 |  | 5.49 | 5.43 | 5.44
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 21
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.4 | 76.4 | 76.7 | 72.5 | 70.8 | 71.8 | 73.5 |  | 73.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 | 0 | 0 | 0 | 0 | 0.1 | 0.1 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.2 | 71.7 | 71.4 | 68.4 | 67.8 | 69.1 | 68.7 |  | 68.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66 | 66 | 68.8 | 63.9 | 62.8 | 64.4 | 65.4 |  | 72.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 44.8 | 49 | 48.8 | 37.1 | 36.8 | 33.7 | 30.6 |  | 48.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 117.9 | 115 | 116.9 | 117.4 | 115.8 | 116.9 | 115.5 |  | 117.2
| INPUT | Kw | 1194kW |  | 1164 | 1163 | 1184 | 1189 | 1172 | 1188 | 1177 |  | 1196
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46848.6 | 47741.7 | 47731.9 | 45355.3 | 45345.4 | 47669.3 | 47659.5 |  | 46969.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 59.5 | 59 | 59 | 57.9 | 57.7 | 57.4 | 57.6 |  | 58.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.49 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 46 | 45.1 | 45.2 | 45.1 | 45 | 44 | 44.9 |  | 45.2
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.22 | 0.23 | 0.23 | 0.23 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 | 3.3 | 3.6 | 4.5 | 4.2 | 4.2 | 3.9 |  | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 | 2.4 | 2.8 | 3.4 | 3.6 | 3.2 | 2.8 |  | 3.3
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 2.2 | 2 | 1.1 | 0.7 | 1.3 | 1.2 | 0 | 1.2 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 671.9 | 674.56 | 654.54 | 628.64 | 633 | 719.92 | 649.9 |  | 647.7
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.4 | 12.5 | 13.5 | 13.5 | 13.3 | 12.8 | 12.8 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 | 4.6 | 4.8 | 4.5 | 4.3 | 4.5 | 4 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.8 | 7.9 | 8.7 | 9 | 9 | 8.3 | 8.8 | 0 | 9 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6827.6212 | 6153.6074 | 6575.6328 | 6533.2102 | 6578.5219 | 6899.9261 | 6604.0647 | 0 | 6731.2933 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.85 | 0.85 | 0.84 | 0.84 | 0.85 | 0.84 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 | 36.7 | 36.9 | 36.6 | 36.5 | 37 | 36.9 |  | 36.6
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.9 | 37.6 | 37.9 | 37.1 | 37.2 | 37.5 | 37.4 |  | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.7 | 4.6 | 4.4 | 3.6 | 2.8 | 4.3 | 3.5 | 0 | 2.3 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.9 | 28 | 28.8 | 28.2 | 28.9 | 27.9 | 28.8 |  | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.2 | 33 | 33.5 | 33.5 | 34.4 | 33.2 | 33.9 |  | 34.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 5 | 4.7 | 5.3 | 5.5 | 5.3 | 5.1 | 0 | 6 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1298.9 | 1299.34 | 1296.5 | 1293.88 | 1298.1 | 1272.32 | 1287.1 |  | 1110.7
| HEAT CAPACITY | kW | 8226.9 | 0 | 7949.388 | 7501.963 | 7036.4319 | 7918.6651 | 8244.2841 | 7786.7159 | 7579.9192 | 0 | 7695.3811 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.46 | 0.47 | 0.46 | 0.47 | 0.47 | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 | 19.6 | 19.9 | 19.3 | 20 | 20.2 | 20.1 |  | 19.9
| LIQUID LEVEL | mm | mm |  | 173.4 | 126.4 | 129.8 | 208.2 | 202.2 | 214.5 | 207.3 |  | 155.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.4 | 5.25 | 5.3 | 5.54 | 5.72 | 5.14 | 5.59 |  | 5.49
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 22
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 72.9 |  | 75.5 |  | 73.8 |  | 73.1 |  | 73.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.4 |  | 0 |  | 0 |  | 0.1 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.8 |  | 71.3 |  | 69 |  | 68.1 |  | 68
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.7 |  | 68.8 |  | 63.7 |  | 65.1 |  | 72.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 78.1 |  | 71.3 |  | 40.4 |  | 34.1 |  | 52
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 119.1 |  | 118.1 |  | 118.2 |  | 116.6 |  | 118.9
| INPUT | Kw | 1194kW |  | 1161 |  | 1183 |  | 1183 |  | 1180 |  | 1200
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46858 |  | 47749 |  | 45364 |  | 47683 |  | 46979
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.1 |  | 57.7 |  | 57.5 |  | 58.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.6 |  | 45.2 |  | 46 |  | 44.9 |  | 44.6
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.8 |  | 4 |  | 4 |  | 4.7
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.6 |  | 2.5 |  | 3.3 |  | 3 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0 | 2.2 | 0 | 1.1 | 0 | 1 | 0 | 1 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 677.68 |  | 656.64 |  | 629.04 |  | 639.44 |  | 671.28
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.9 |  | 13.1 |  | 13.4 |  | 13.2 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.4 |  | 4.7 |  | 4.4 |  | 4 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.5 | 0 | 8.4 | 0 | 9 | 0 | 9.2 | 0 | 8.6 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6651.5935 | 0 | 6369.2564 | 0 | 6537.3672 | 0 | 6793.127 | 0 | 6666.291 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.86 |  | 0.85 |  | 0.85 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 |  | 36.5 |  | 36 |  | 36.4 |  | 36.1
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.9 |  | 38 |  | 37.4 |  | 37.5 |  | 37.1
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 3.3 | 0 | 4.7 | 0 | 3.7 | 0 | 4 | 0 | 3.1 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.4 |  | 28.3 |  | 28.3 |  | 28.3 |  | 28.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.6 |  | 33.3 |  | 33.7 |  | 33.5 |  | 34
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 0 | 5 | 0 | 5.4 | 0 | 5.2 | 0 | 5.7 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1293.74 |  | 1298.08 |  | 1293.74 |  | 1296.54 |  | 1136.94
| HEAT CAPACITY | kW | 8226.9 | 0 | 7768.4157 | 0 | 7494.6882 | 0 | 8067.2009 | 0 | 7785.2286 | 0 | 7483.3233 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.46 |  | 0.46 |  | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.9 |  | 19.7 |  | 19.6 |  | 20 |  | 19.6
| LIQUID LEVEL | mm | mm |  | 218 |  | 124 |  | 207.2 |  | 224.5 |  | 162.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.48 |  | 5.15 |  | 5.65 |  | 5.58 |  | 5.26
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 23
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 72.6 | 80 | 78.6 |  | 74 | 72.4 | 76.1 | 72.9 | 77.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.4 | 0 | 0 |  | 0 | 0 | 0.2 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 67.9 | 75.5 | 74 |  | 68.9 | 69.6 | 71.2 | 69.1 | 73.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 62 | 64.5 | 65 |  | 59.4 | 64.1 | 63 | 69.2 | 68.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 88.1 | 49.2 | 55.1 |  | 40.7 | 33.2 | 36.9 | 49.3 | 52
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 117.6 | 116.5 | 116.7 |  | 118.1 | 118.8 | 118.9 | 116.5 | 118.6
| INPUT | Kw | 1194kW |  | 1151 | 1182 | 1178 |  | 1189 | 1201 | 1208 | 1179 | 1206
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46882.7 | 47770.8 | 47759 |  | 45388.9 | 47705.5 | 47693.7 | 47011.2 | 46999.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 | 59.2 | 59.1 |  | 57.6 | 57.4 | 57.4 | 58.6 | 58.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.49 |  | 0.59 | 0.52 | 0.59 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.7 | 44.8 | 44.7 |  | 45 | 44.9 | 45 | 45 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.22 | 0.21 | 0.21 |  | 0.23 | 0.22 | 0.22 | 0.22 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 | 3 | 3.2 |  | 4 | 4.5 | 4.3 | 3.9 | 3.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.2 | 2.1 | 2.3 |  | 3.3 | 3.6 | 3 | 2.9 | 2.8
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 2.4 | 1.8 | 0 | 1.2 | 1.2 | 1.3 | 1.2 | 1.1 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 677.2 | 675 | 660.56 |  | 664.96 | 733.9 | 731.12 | 685.4 | 676.8
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.2 | 12.5 | 12.4 |  | 13 | 12.7 | 12.6 | 12.8 | 12.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.1 | 4.5 | 4.1 |  | 4.5 | 4.8 | 4.3 | 4.1 | 3.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.1 | 8 | 8.3 | 0 | 8.5 | 7.9 | 8.3 | 8.7 | 8.5 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6334.0878 | 6235.5658 | 6331.0023 | 0 | 6526.7436 | 6694.9307 | 7007.2702 | 6885.6582 | 6642.9561 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 | 0.84 | 0.84 |  | 0.84 | 0.84 | 0.84 | 0.83 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.5 | 36.7 | 36.3 |  | 36.4 | 36.9 | 36.4 | 36 | 35.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36 | 37.5 | 37.2 |  | 37.3 | 37.1 | 37 | 36.4 | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 3.3 | 4.3 | 4.8 | 0 | 4.4 | 3.3 | 4.4 | 2.4 | 3.2 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.7 | 28.3 | 27.5 |  | 27.5 | 28.6 | 27.3 | 28.4 | 27.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 32.7 | 33.2 | 32.4 |  | 32.9 | 33.8 | 32.6 | 34 | 33.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5 | 4.9 | 4.9 | 0 | 5.4 | 5.2 | 5.3 | 5.6 | 5.7 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1294.44 | 1306.6 | 1302.56 |  | 1296.68 | 1299.2 | 1295.7 | 1198.3 | 1141.14
| HEAT CAPACITY | kW | 8226.9 | 0 | 7473.6721 | 7393.0023 | 7370.1432 | 0 | 8085.5335 | 7801.2009 | 7929.8037 | 7748.8222 | 7510.9677 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.45 | 0.45 | 0.45 |  | 0.46 | 0.47 | 0.47 | 0.46 | 0.45
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.7 | 19.2 | 19 |  | 19.7 | 20.3 | 19.9 | 19.2 | 18.9
| LIQUID LEVEL | mm | mm |  | 164.7 | 117.8 | 131.7 |  | 203.9 | 208.2 | 213.3 | 163.2 | 163.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.41 | 5.18 | 5.15 |  | 5.39 | 4.85 | 5.07 | 5.34 | 5.27
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 24
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 67.9 | 71.4 |  | 70.8 | 75.2 | 74.2 | 67.4 | 77 |  | 76.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.2 | 0.2 |  | 0 | 0 | 0 | 0.2 | 0.2 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 64.5 | 67.6 |  | 66.6 | 69.6 | 69.6 | 64.1 | 72.1 |  | 73.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 61.4 | 64.3 |  | 65.9 | 59.9 | 61.9 | 62.8 | 64.7 |  | 69
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 87.3 | 88 |  | 57.6 | 38 | 40.7 | 29.2 | 38.3 |  | 51
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 111.6 | 114.4 |  | 109.7 | 115.3 | 116.6 | 110.8 | 117.5 |  | 117.2
| INPUT | Kw | 1194kW | 1098 | 1131 |  | 1109 | 1180 | 1183 | 1128 | 1205 |  | 1199
COMPRESSOR | RUNNING TIME | Hr | NA | 46901.4 | 46894 |  | 47785 | 45407.6 | 45400 | 47726.8 | 47719.7 |  | 47019.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 57.9 | 58.1 |  | 58.8 | 57.7 | 57.5 | 57.3 | 57.3 |  | 58.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.48 | 0.58 | 0.59 | 0.52 | 0.52 |  | 0.47
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.7 | 44.7 |  | 45 | 45 | 44.9 | 45.3 | 44.3 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.22 |  | 0.21 | 0.22 | 0.22 | 0.22 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.3 | 3.6 |  | 3.1 | 3.8 | 3.9 | 3.7 | 4.2 |  | 3.8
| SATURATION TEMPERATURE | CELCIUS | C | 2.8 | 2.8 |  | 2.4 | 3 | 3.2 | 3 | 3.4 |  | 2.2
| APPROACH TEMP | CELCIUS | C | 1.1 | 1.3 | 0 | 1.8 | 0.7 | 0.9 | 1 | 0.8 | 0 | 1.9 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 690.4 | 651.7 |  | 661.3 | 681.84 | 667.8 | 686.7 | 728.5 |  | 675.3
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.3 | 12.5 |  | 12.3 | 12.1 | 12.8 | 12.1 | 12.5 |  | 12.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 3.9 | 4.1 |  | 4.2 | 3.7 | 4.1 | 4 | 4.2 |  | 4.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.4 | 8.4 | 0 | 8.1 | 8.4 | 8.7 | 8.1 | 8.3 | 0 | 8.5 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 6696.7206 | 6321.3395 | 0 | 6185.3695 | 6613.6905 | 6708.8453 | 6422.9446 | 6982.1594 | 0 | 6628.2333 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.79 |  | 0.8 | 0.83 | 0.87 | 0.81 | 0.81 |  | 0.7
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.1 | 34.7 |  | 34.9 | 36.3 | 35.7 | 35.8 | 35.2 |  | 34.9
| SATURATED TEMEPRATURE | CELCIUS | C | 35.6 | 35.1 |  | 35.9 | 37 | 36.5 | 36.3 | 36.1 |  | 35.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.5 | 2.5 | 0 | 4.2 | 3.9 | 4 | 3.5 | 3.6 | 0 | 2.4 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.9 | 27.1 |  | 27 | 27.8 | 27.1 | 27.8 | 27.1 |  | 36.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.1 | 32.6 |  | 31.7 | 33.1 | 32.5 | 32.8 | 32.5 |  | 33.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.2 | 5.5 | 0 | 4.7 | 5.3 | 5.4 | 5 | 5.4 | 0 | -3.8 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1277.1 | 1288.6 |  | 1298.3 | 1310.1 | 1291.3 | 1266.4 | 1289.8 |  | 1145.3
| HEAT CAPACITY | kW | 8226.9 | 7668.4988 | 8183.9492 | 0 | 7046.2009 | 8017.933 | 8051.9861 | 7311.7783 | 8042.6328 | 0 | -5025.5658 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.45 |  | 0.44 | 0.46 | 0.46 | 0.46 | 0.46 |  | 0.44
| SATURATED TEMPERATURE | CELCIUS | C | 19.7 | 18.5 |  | 18.7 | 19.4 | 19.3 | 19.5 | 19.3 |  | 18.2
| LIQUID LEVEL | mm | mm | 233.4 | 206.8 |  | 120.5 | 201.7 | 199.7 | 213.8 | 212.7 |  | 153.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.66 | 5.63 |  | 5.5 | 5.24 | 5.56 | 5.37 | 5.17 |  | 5.46
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 25
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 68.6 | 71.4 |  | 77.8 | 68.5 | 72 | 75.2 | 71 |  | 76.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.8 | 0.8 |  | 0 | 0 | 0 | 0.1 | 0.2 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 65.2 | 65.9 |  | 73.5 | 63.7 | 66 | 70.8 | 66.8 |  | 71.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 62.4 | 65.8 |  | 67.9 | 59.8 | 63.7 | 60 | 66.2 |  | 71.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 87.6 | 77.2 |  | 54.1 | 39.3 | 38.1 | 33 | 30.6 |  | 53.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 112.3 | 117.2 |  | 116.6 | 110.3 | 115.3 | 116.6 | 114.7 |  | 119.4
| INPUT | Kw | 1194kW | 1107 | 1144 |  | 1177 | 1118 | 1164 | 1180 | 1167 |  | 1214
COMPRESSOR | RUNNING TIME | Hr | NA | 46920.1 | 46911 |  | 47793.7 | 45426 | 45416.8 | 47745.8 | 47736.7 |  | 47028.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.8 | 58 |  | 59.3 | 57.5 | 57.5 | 57.3 | 57.4 |  | 58.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.51 | 0.53 |  | 0.49 | 0.58 | 0.59 | 0.52 | 0.52 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.4 | 44.7 |  | 44.7 | 45.3 | 44.8 | 44.8 | 44.9 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.21 | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.2 | 4.4 |  | 3.5 | 3.6 | 4.2 | 3.7 | 4.1 |  | 4.4
| SATURATION TEMPERATURE | CELCIUS | C | 2.6 | 3.8 |  | 2.5 | 2.9 | 3.5 | 3.3 | 3.3 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 1.2 | 0.8 | 0 | 2.5 | 1.4 | 0.7 | 0.3 | 1.1 | 0 | 0.9 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 688.16 | 680.7 |  | 660.9 | 677.84 | 649.97 | 741.84 | 629.7 |  | 679.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 11.3 | 13.4 |  | 13.4 | 12 | 13 | 11.7 | 13.3 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 3.8 | 4.6 |  | 5 | 4.3 | 4.2 | 3.6 | 4.4 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.5 | 8.8 | 0 | 8.4 | 7.7 | 8.8 | 8.1 | 8.9 | 0 | 9 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 5959.8152 | 6917.0439 | 0 | 6410.5774 | 6026.9838 | 6604.776 | 6938.6882 | 6471.5127 | 0 | 7065.9353 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.78 | 0.81 |  | 0.84 | 0.8 | 0.83 | 0.82 | 0.82 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.7 | 35.7 |  | 36.4 | 35.6 | 36.5 | 35.8 | 36.2 |  | 35.9
| SATURATED TEMEPRATURE | CELCIUS | C | 34.7 | 36.1 |  | 37.2 | 35.8 | 37.1 | 36.2 | 36.6 |  | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 3 | 2.6 | 0 | 4.2 | 4.1 | 3.8 | 4.3 | 3.5 | 0 | 2.5 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 26.9 | 28.2 |  | 28 | 26.7 | 28.1 | 26.6 | 27.9 |  | 27.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 31.7 | 33.5 |  | 33 | 31.7 | 33.3 | 31.9 | 33.1 |  | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 4.8 | 5.3 | 0 | 5 | 5 | 5.2 | 5.3 | 5.2 | 0 | 6 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1268.26 | 1305.4 |  | 1300.1 | 1275.4 | 1314.5 | 1269.52 | 1291.8 |  | 1141.1
| HEAT CAPACITY | kW | 8226.9 | 7029.6166 | 7989.1686 | 0 | 7506.351 | 7363.7413 | 7893.0716 | 7769.5797 | 7756.7667 | 0 | 7906.0046 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.46 |  | 0.46 | 0.46 | 0.47 | 0.46 | 0.46 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 18.8 | 19.5 |  | 19.2 | 19.1 | 20 | 19.8 | 19.8 |  | 19.4
| LIQUID LEVEL | mm | mm | 184 | 180.7 |  | 134.4 | 199.4 | 209.6 | 213 | 218.4 |  | 170.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.39 | 5.66 |  | 5.31 | 5.41 | 5.61 | 4.81 | 5.64 |  | 5.48
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 26
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 71 |  | 77 | 75.3 | 70.8 | 71.4 | 74.3 | 74.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.8 |  | 0 | 0 | 0 | 0.1 | 0.1 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.3 |  | 72.7 | 70.8 | 67 | 66 | 68.8 | 69.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.5 |  | 70.4 | 63.8 | 63.6 | 66.8 | 65.6 | 78.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 83.1 |  | 51.4 | 41.7 | 35 | 32.8 | 32 | 58.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 117.5 |  | 116.9 | 116.9 | 116.4 | 112.9 | 116.6 | 115.8
| INPUT | Kw | 1194kW |  | 1156 |  | 1186 | 1183 | 1190 | 1140 | 1189 | 1171
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46926.4 |  | 47803.6 | 45443 | 45435 | 47769 | 47760.9 | 47042
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.5 |  | 59.1 | 57.9 | 57.9 | 57.3 | 57.4 | 58.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.58 | 0.59 | 0.52 | 0.52 | 0.47
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 |  | 45 | 44.5 | 45 | 45 | 45.1 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 | 0.22 | 0.23 | 0.22 | 0.22 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.5 |  | 3.8 | 3.7 | 4.5 | 3.7 | 3.9 | 4.2
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.8 | 3.1 | 3.6 | 2.8 | 2.9 | 3.2
| APPROACH TEMP | CELCIUS | C | 0 | 1.2 | 0 | 2.4 | 1.5 | 0.7 | 1.5 | 1.2 | 0.9 | 0 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 647.5 |  | 639.5 | 678.6 | 644.6 | 710.24 | 641.8 | 687.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.7 |  | 13.9 | 13.2 | 13 | 12.9 | 13.1 | 12.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 |  | 5.2 | 4.6 | 4.3 | 4.3 | 4.1 | 4.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.7 | 0 | 8.7 | 8.6 | 8.7 | 8.6 | 9 | 8.5 | 0 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6504.9076 | 0 | 6424.5381 | 6738.9838 | 6475.7737 | 7053.1917 | 6669.9769 | 6748.9607 | 0 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 |  | 0.85 | 0.81 | 0.85 | 0.79 | 0.84 | 0.79
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.4 |  | 37 | 35.4 | 37.2 | 35 | 37 | 34.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.8 | #REF! | 37.8 | 36.2 | 37.8 | 35.5 | 37.5 | 34.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.4 |  | 4.3 | 3.9 | 3.9 | 3.6 | 3.5 | 2.5 | 0 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.6 |  | 28.6 | 36.8 | 28.7 | 26.8 | 28.7 | 26.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.4 |  | 33.5 | 32.3 | 33.9 | 31.9 | 34 | 32.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.8 | 0 | 4.9 | -4.5 | 5.2 | 5.1 | 5.3 | 5.7 | 0 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1253.1 |  | 1286.7 | 1305.9 | 1296.3 | 1303.4 | 1233.5 | 1233.5
| HEAT CAPACITY | kW | 8226.9 | 0 | 8392.5866 | 0 | 7280.4042 | -6785.8545 | 7783.7875 | 7675.9122 | 7549.1339 | 8118.8799 | 0 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.47 | 0.45 | 0.47 | 0.45 | 0.47 | 0.44
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.3 |  | 20 | 18.9 | 20 | 19.2 | 20.2 | 18.6
| LIQUID LEVEL | mm | mm |  | 204.7 |  | 124 | 212.3 | 203.1 | 206.4 | 207.3 | 158.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.67 |  | 5.57 | 5.75 | 5.42 | 5.85 | 5.54
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 27
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK |  | OK | 47069.4 | OK
OPENING OF VANE |  | % | 0~100% | 77.3 | 72 | 69.3 | 75.1 |  | 73.9 |  | 74.1 | 74.6 | 72.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0.6 | 0 | 0 |  | 0 |  | 0.1 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% | 72.4 | 66.9 | 65.4 | 70.1 |  | 68.7 |  | 69.1 | 70.1 | 67.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 60.7 | 64.2 | 62.5 | 66.1 |  | 63.1 |  | 63.8 | 66.6 | 69.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 100 | 48.1 | 50.4 | 53.8 |  | 39.9 |  | 33.7 | 53.2 | 55.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 114.7 | 118.3 | 109 | 116.4 |  | 115.9 |  | 117.2 | 116.8 | 116.4
| INPUT | Kw | 1194kW | 1129 | 1156 | 1111 | 1176 |  | 1182 |  | 1201 | 1183 | 1192
COMPRESSOR | RUNNING TIME | Hr | NA | 46947.2 | 46935.9 | 47824.6 | 47813.1 |  | 45451.1 |  | 47778 | 47069.4 | 47050.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.6 | 58 | 58.9 | 59.1 |  | 57.9 |  | 57.1 | 58.6 | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.51 | 0.52 | 0.49 | 0.49 |  | 0.59 |  | 0.53 | 0.47 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.6 | 45.2 | 45.1 | 45.1 |  | 44.9 |  | 45.1 | 45.1 | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.21 | 0.23 | 0.21 | 0.21 |  | 0.23 |  | 0.23 | 0.22 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 2.1 | 4.2 | 3.3 | 3.1 |  | 4.6 |  | 4.4 | 3.8 | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 1.8 | 3.8 | 2.4 | 2.4 |  | 3.6 |  | 3.5 | 2.4 | 3.8
| APPROACH TEMP | CELCIUS | C | 2.2 | 0.9 | 1.9 | 2.4 | 0 | 0.6 | 0 | 1.3 | 1.5 | 1.2 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 691.7 | 710.5 | 676.6 | 686 |  | 660.5 |  | 712.4 | 688.8 | 717.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12 | 13.3 | 12.2 | 13.3 |  | 13.1 |  | 13.3 | 12.1 | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4 | 4.7 | 4.3 | 4.8 |  | 4.2 |  | 4.8 | 3.9 | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8 | 8.6 | 7.9 | 8.5 | 0 | 8.9 | 0 | 8.5 | 8.2 | 8.3 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 6389.8383 | 7055.7737 | 6172.2171 | 6733.2564 | 0 | 6788.0485 | 0 | 6992.3788 | 6522.1247 | 6880.5658 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.8 | 0.84 | 0.84 |  | 0.82 |  | 0.83 | 0.81 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.8 | 35.5 | 36.4 | 36.4 |  | 35.8 |  | 37.1 | 36.5 | 36.1
| SATURATED TEMEPRATURE | CELCIUS | C | 36.4 | 36 | 37.3 | 37.4 |  | 36.5 |  | 37.1 | 36.8 | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.3 | 2.2 | 4.1 | 4.5 | 0 | 2.8 | 0 | 3.5 | 2.3 | 2.4 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.8 | 28.3 | 28.8 | 28.1 |  | 28.1 |  | 28.1 | 28.7 | 28
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.1 | 33.8 | 33.2 | 32.9 |  | 33.7 |  | 33.6 | 34.5 | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.3 | 5.5 | 4.4 | 4.8 | 0 | 5.6 | 0 | 5.5 | 5.8 | 6.1 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1296.4 | 1263.2 | 1302.2 | 1309.7 |  | 1295.4 |  | 1241.6 | 1135.5 | 1079.4
| HEAT CAPACITY | kW | 8226.9 | 7934.0878 | 8022.6328 | 6616.2587 | 7259.3072 | 0 | 8376.7206 | 0 | 7885.4503 | 7604.9654 | 7603.164 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.46 | 0.46 | 0.45 |  | 0.45 |  | 0.47 | 0.46 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 18.9 | 19.6 | 19.6 | 19.2 |  | 19.3 |  | 20.2 | 19.3 | 20.1
| LIQUID LEVEL | mm | mm | 350 | 192 | 121.5 | 127 |  | 204.5 |  | 199.1 | 152.5 | 151.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.25 | 5.35 | 5.21 | 5.15 |  | 5.56 |  | 5.18 | 5.12 | 5.13
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 28
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 71.1 | 72.1 |  | 80.5 | 70 | 72.1 | 76.1 | 73.1 |  | 74.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.8 | 0.4 |  | 0 | 0 | 0 | 0.1 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% | 66.8 | 65.8 |  | 76.7 | 67 | 66.3 | 71.4 | 69.5 |  | 68.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 61.4 | 68 |  | 69 | 59 | 63.7 | 60.2 | 65 |  | 73.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 89 | 58.2 |  | 47.9 | 37.9 | 38.2 | 34.5 | 33.2 |  | 47.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 112.3 | 119.1 |  | 119.5 | 112 | 116.2 | 117 | 116.7 |  | 118.5
| INPUT | Kw | 1194kW | 1120 | 1165 |  | 1205 | 1140 | 1175 | 1188 | 1185 |  | 1205
COMPRESSOR | RUNNING TIME | Hr | NA | 46964 | 46674.2 |  | 47573.6 | 45475.9 | 45170.5 | 47797.7 | 474777.5 |  | 46796
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.8 |  | 59.3 | 57.4 | 57.6 | 57.3 | 57.5 |  | 58.8
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 | 0.58 | 0.59 | 0.52 | 0.52 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 11.8 | 44.8 |  | 45 | 45.6 | 44.8 | 45.1 | 45 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.22 | 0.23 |  | 0.22 | 0.22 | 0.23 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.3 | 4.4 |  | 3.4 | 3.6 | 4.4 | 3.7 | 3.8 |  | 4.6
| SATURATION TEMPERATURE | CELCIUS | C | 2.5 | 3.9 |  | 2.5 | 2.9 | 3.6 | 2.7 | 2.7 |  | 3.5
| APPROACH TEMP | CELCIUS | C | 1.2 | 1.1 | 0 | 2.5 | 0.7 | 0.7 | 1.3 | 1.3 | 0 | 1.2 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 690.3 | 680.9 |  | 661.2 | 679.1 | 633.5 | 744.2 | 642.3 |  | 649.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 11.9 | 13.4 |  | 13.6 | 11.8 | 13.3 | 11.9 | 12.8 |  | 13.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 3.7 | 5 |  | 5 | 3.6 | 4.3 | 4 | 4 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.2 | 8.4 | 0 | 8.6 | 8.2 | 9 | 7.9 | 8.8 | 0 | 9 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 6536.3279 | 6604.5727 | 0 | 6566.1894 | 6430.2771 | 6583.7182 | 6788.8915 | 6526.836 | 0 | 6748.9607 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.79 | 0.83 |  | 0.86 | 0.82 | 0.84 | 0.82 | 0.85 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.2 | 36.6 |  | 37.3 | 36 | 36.7 | 36 | 37.1 |  | 36.9
| SATURATED TEMEPRATURE | CELCIUS | C | 35.5 | 37.1 |  | 38.2 | 36.6 | 37.4 | 36.5 | 37.5 |  | 37.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.4 | 2.5 | 0 | 4.3 | 3.8 | 2.8 | 3.6 | 3.4 | 0 | 2.3 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.5 | 29 |  | 29 | 27.6 | 29.1 | 27.7 | 29 |  | 28.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.1 | 34.6 |  | 33.9 | 32.8 | 34.6 | 32.9 | 34.1 |  | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 5.6 | 0 | 4.9 | 5.2 | 5.5 | 5.2 | 5.1 | 0 | 6 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1273.6 | 1296.4 |  | 1306.6 | 1298.3 | 1300.4 | 1262.1 | 1298 |  | 1137.8
| HEAT CAPACITY | kW | 8226.9 | 8235.7506 | 8383.1871 | 0 | 7393.0023 | 7795.7968 | 8258.8915 | 7578.4296 | 7644.1109 | 0 | 7883.1409 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.48 |  | 0.46 | 0.46 | 0.47 | 0.46 | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 18.9 | 20.5 |  | 19.8 | 19.4 | 20.2 | 19.4 | 20 |  | 20.2
| LIQUID LEVEL | mm | mm | 205.8 | 210.6 |  | 123.8 | 191.2 | 208.2 | 201.3 | 211.2 |  | 164.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.4 | 5.3 |  | 5.36 | 5.32 | 5.67 | 4.89 | 5.42 |  | 5.52
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 29
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 71.4 | 80.1 | 76.7 |  | 70.8 | 71.8 | 73.5 | 73.7 | 73.4
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 | 0 | 0 |  | 0 | 0.1 | 0.1 | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.2 | 75.4 | 71.4 |  | 67.8 | 69.1 | 68.7 | 68.5 | 68.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66 | 68.3 | 68.8 |  | 62.8 | 65 | 65.4 | 72.9 | 72.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 44.8 | 51.6 | 48.8 |  | 36.8 | 31.2 | 30.6 | 57.8 | 48.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 117.9 | 116.4 | 116.9 |  | 115.8 | 115.3 | 115.5 | 117 | 117.2
| INPUT | Kw | 1194kW |  | 1164 | 1193 | 1184 |  | 1172 | 1169 | 1177 | 1185 | 1196
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46974.2 | 47855.5 | 47846.6 |  | 45490.2 | 47811.1 | 47802.1 | 47095.3 | 47086.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 59.5 | 59.2 | 59 |  | 57.7 | 57.3 | 57.6 | 58.7 | 58.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.49 |  | 0.59 | 0.52 | 0.52 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 46 | 45 | 45.2 |  | 45 | 45 | 44.9 | 45.1 | 45.2
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.22 |  | 0.23 | 0.22 | 0.22 | 0.22 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.3 | 3.5 | 3.6 |  | 4.2 | 4 | 3.9 | 4.5 | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 | 2.5 | 2.8 |  | 3.6 | 2.9 | 2.8 | 3.6 | 3.3
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 2.3 | 2 | 0 | 0.7 | 1.1 | 1.2 | 1.1 | 1.2 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 678.8 | 674.3 | 664.3 |  | 668.1 | 652.9 | 675.9 | 686.9 | 678.5
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.4 | 13.2 | 13.5 |  | 13.3 | 13 | 12.8 | 13.1 | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 | 4.8 | 4.8 |  | 4.3 | 4 | 4 | 4.7 | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.8 | 8.4 | 8.7 | 0 | 9 | 9 | 8.8 | 8.4 | 9 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6897.7367 | 6540.5543 | 6673.6836 | 0 | 6943.3025 | 6785.3349 | 6868.2679 | 6662.7714 | 7051.3857 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.85 | 0.85 |  | 0.84 | 0.83 | 0.84 | 0.84 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 | 36.7 | 36.9 |  | 36.5 | 36.4 | 36.9 | 35.7 | 36.6
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.9 | 37.5 | 37.9 |  | 37.2 | 36.8 | 37.4 | 36.2 | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.7 | 4.4 | 4.4 | 0 | 2.8 | 3.6 | 3.5 | 2.4 | 2.3 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.9 | 28.2 | 28.8 |  | 28.9 | 28.3 | 28.8 | 28 | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.2 | 33.1 | 33.5 |  | 34.4 | 33.2 | 33.9 | 33.8 | 34.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 4.9 | 4.7 | 0 | 5.5 | 4.9 | 5.1 | 5.8 | 6 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1294.1 | 1307.2 | 1304.5 |  | 1315.8 | 1302.5 | 1299.3 | 1198.7 | 1141.2
| HEAT CAPACITY | kW | 8226.9 | 0 | 7920.0115 | 7396.3972 | 7079.8499 | 0 | 8356.6975 | 7369.8037 | 7651.7667 | 8028.2448 | 7906.6975 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.46 | 0.47 |  | 0.47 | 0.46 | 0.47 | 0.46 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 | 19.3 | 19.9 |  | 20 | 19.7 | 20.1 | 19.3 | 19.9
| LIQUID LEVEL | mm | mm |  | 173.4 | 111.8 | 129.8 |  | 202.2 | 206.5 | 207.3 | 154.9 | 155.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.4 | 5.1 | 5.3 |  | 5.72 | 5.58 | 5.59 | 5.2 | 5.49
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 30
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 72.9 |  | 80.7 |  | 74.9 |  | 71.8 |  | 74.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.2 |  | 0 |  | 0 |  | 0.1 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.8 |  | 77.2 |  | 70.2 |  | 69.1 |  | 69.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 65.4 |  | 67.3 |  | 63.6 |  | 65.1 |  | 72.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 83.8 |  | 49.7 |  | 37.1 |  | 32 |  | 50.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 118.4 |  | 117.8 |  | 117.6 |  | 115.2 |  | 118.7
| INPUT | Kw | 1194kW |  | 1164 |  | 1196 |  | 1198 |  | 1172 |  | 1204
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46984 |  | 47870 |  | 45500 |  | 47826 |  | 47104
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.8 |  | 59.2 |  | 57.8 |  | 57.5 |  | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 |  | 0.58 |  | 0.52 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 |  | 45 |  | 45 |  | 45 |  | 44.6
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.22 |  | 0.21 |  | 0.23 |  | 0.23 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.3 |  | 4.3 |  | 3.8 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 2.9 |  | 1.8 |  | 3.3 |  | 3.1 |  | 2.8
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 0 | 2.1 | 0 | 1.1 | 0 | 1.1 | 0 | 1 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 666.08 |  | 649.6 |  | 654.16 |  | 716.4 |  | 663.04
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.4 |  | 12.4 |  | 13 |  | 12.7 |  | 12.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 3.9 |  | 3.9 |  | 4.4 |  | 4.2 |  | 3.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.5 | 0 | 8.5 | 0 | 8.6 | 0 | 8.5 | 0 | 8.6 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6537.7367 | 0 | 6375.9815 | 0 | 6496.2771 | 0 | 7031.6397 | 0 | 6584.4619 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.79 |  | 0.82 |  | 0.82 |  | 0.82 |  | 0.8
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.1 |  | 36.7 |  | 37 |  | 36.5 |  | 36.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.4 |  | 36.6 |  | 36.6 |  | 36.4 |  | 35.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 3.3 | 0 | 4.8 | 0 | 4.4 | 0 | 4.4 | 0 | 3.2 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27 |  | 26.8 |  | 26.9 |  | 26.7 |  | 26.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 32.1 |  | 31.8 |  | 32.2 |  | 32 |  | 32.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.1 | 0 | 5 | 0 | 5.3 | 0 | 5.3 | 0 | 5.6 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1293.6 |  | 1301.44 |  | 1308.16 |  | 1291.54 |  | 1138.62
| HEAT CAPACITY | kW | 8226.9 | 0 | 7618.1986 | 0 | 7514.0878 | 0 | 8006.06 | 0 | 7904.3441 | 0 | 7362.9007 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.46 |  | 0.47 |  | 0.46 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.7 |  | 19.3 |  | 20 |  | 19.8 |  | 19.7
| LIQUID LEVEL | mm | mm |  | 167 |  | 131.9 |  | 205.5 |  | 212.5 |  | 158.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.46 |  | 5.35 |  | 5.57 |  | 5.57 |  | 5.33
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 31
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 73.3 | 80 | 77.1 | 72.7 | 74.6 | 75.1 | 74 |  | 73
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0 | 0 | 0 | 0 | 0.2 | 0.1 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 67.5 | 75.5 | 72.1 | 67.8 | 69.1 | 70 | 70.6 |  | 67.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 68.2 | 64.5 | 69.9 | 61.4 | 63.2 | 62.7 | 65.7 |  | 73.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 97.7 | 49.2 | 54.5 | 39.5 | 38.9 | 34.5 | 33.5 |  | 50.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 118.5 | 116.5 | 117.7 | 115.8 | 118.3 | 119.2 | 116.4 |  | 117.8
| INPUT | Kw | 1194kW |  | 1156 | 1182 | 1186 | 1180 | 1193 | 1208 | 1180 |  | 1194
COMPRESSOR | RUNNING TIME | Hr | NA |  | 47002.2 | 47890.9 | 47880.7 | 45534.6 | 45524.4 | 47846.5 | 47836.3 |  | 47126.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 | 59.2 | 59.2 | 57.8 | 57.5 | 57.4 | 57.4 |  | 58.7
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.84 | 0.59 | 0.59 | 0.53 | 0.52 |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.2 | 44.8 | 44.7 | 45 | 44.8 | 45.1 | 44.9 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.22 | 0.23 | 0.23 | 0.22 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 3.9 | 3 | 3.9 | 4.3 | 4.1 | 4.4 | 3.8 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.6 | 2.1 | 2.9 | 3.4 | 3.3 | 3.4 | 3.1 |  | 3.1
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 2.4 | 1.9 | 0.7 | 1.2 | 1.3 | 0.8 | 0 | 1.5 | 0 | 0
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 682.72 | 676.8 | 659.2 | 681.7 | 634.08 | 745.5 | 639.6 |  | 669.76
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.2 | 12.5 | 13.2 | 12.6 | 13.4 | 12.7 | 13.2 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 | 4.5 | 4.8 | 4.1 | 4.5 | 4.7 | 3.9 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.6 | 8 | 8.4 | 8.5 | 8.9 | 8 | 9.3 | 0 | 8.6 | 0 | 0
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6779.8984 | 6252.194 | 6394.0878 | 6691.0508 | 6516.5266 | 6886.836 | 6868.6836 | 0 | 6651.1963 | 0 | 0
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.84 | 0.84 | 0.83 | 0.84 | 0.84 | 0.83 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.8 | 36.7 | 36.6 | 36.2 | 36.8 | 36.9 | 36.5 |  | 36.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.3 | 37.5 | 37.4 | 36.9 | 37.4 | 37.4 | 36.9 |  | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 3.3 | 4.3 | 4.8 | 2.9 | 4.4 | 3.6 | 4.3 | 0 | 3.2 | 0 | 0
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.8 | 28.3 | 27.6 | 28.5 | 27.7 | 28.5 | 27.5 |  | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33 | 33.2 | 32.6 | 34 | 33 | 33.8 | 32.6 |  | 33.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 4.9 | 5 | 5.5 | 5.3 | 5.3 | 5.1 | 0 | 5.7 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1293.18 | 1303.4 | 1297.24 | 1298.2 | 1280.58 | 1267.5 | 1293.74 |  | 1145.06
| HEAT CAPACITY | kW | 8226.9 | 0 | 7765.0531 | 7374.8961 | 7489.8383 | 8244.9192 | 7837.2679 | 7757.2171 | 7619.0231 | 0 | 7536.7691 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.45 | 0.46 | 0.46 | 0.47 | 0.47 | 0.45 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.9 | 19.2 | 19.7 | 19.5 | 20.2 | 20.3 | 19.7 |  | 19.8
| LIQUID LEVEL | mm | mm |  | 240.7 | 117.8 | 126.2 | 205.2 | 209.5 | 215.7 | 194.7 |  | 161
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.58 | 5.18 | 5.32 | 5.29 | 5.65 | 4.86 | 5.72 |  | 5.46
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO