## 1
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK |  |  | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 71.4 | 82.5 | 76.4 |  |  |  |  | 73.4 | 73.7 | 78.7 | 77.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.4 | 0 | 0 |  |  |  |  | 0 | 0.1 | 0.1 | 0.1
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.7 | 79.1 | 72 |  |  |  |  | 68.1 | 68.3 | 75.8 | 72.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 65.4 | 65.9 | 66.9 |  |  |  |  | 70.6 | 65.2 | 71.6 | 72.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 41.7 | 49 | 50.9 |  |  |  |  | 61.8 | 35.9 | 44.8 | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  |  |  |  | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 117.3 | 119.7 | 117 |  |  |  |  | 117.7 | 118.1 | 118.8 | 118.6
| INPUT | Kw | 1194kW |  | 1146 | 1219 | 1183 |  |  |  |  | 1207 | 1202 | 1216 | 1201
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45955.3 | 46885 | 46723.3 |  |  |  |  | 46179 | 46740.9 | 48012 | 47842.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 | 59.5 | 59.1 |  |  |  |  | 58.7 | 57.2 | 59.2 | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.49 |  |  |  |  | 0.49 | 0.53 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 | 44.9 | 44.8 |  |  |  |  | 44.8 | 45 | 45 | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.22 |  |  |  |  | 0.23 | 0.23 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 | 3.5 | 3.8 |  |  |  |  | 4.8 | 4.6 | 4.3 | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 | 2.5 | 2.9 |  |  |  |  | 3.7 | 3.6 | 3.4 | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 2.1 | 2.3 | 0 | 0 | 0 | 0 | 0.9 | 0.4 | 1.5 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 719.1 | 724.32 | 689.3 |  |  |  |  | 756.4 | 714.4 | 733 | 699.7
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.3 | 12.2 | 13.1 |  |  |  |  | 12.2 | 13.1 | 12.4 | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 | 4.6 | 5.2 |  |  |  |  | 4.6 | 5 | 4.9 | 5.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.5 | 7.6 | 7.9 | 0 |  | 0 | 0 | 7.6 | 8.1 | 7.5 | 8.1
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 7058.1409 | 6356.6189 | 6288.0716 | 0 | 0 | 0 | 0 | 6638.1524 | 6682.0323 | 6348.1524 | 6544.5381
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.86 | 0.85 |  |  |  |  | 0.86 | 0.84 | 0.82 | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.1 | 37.3 | 36.7 |  |  |  |  | 36.6 | 37.7 | 36.4 | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 | 38.1 | 37.6 |  |  |  |  | 37 | 37.5 | 36.5 | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.2 | 4.2 | 4.1 | 0 | 0 | 0 | 0 | 2.3 | 3.5 | 2.3 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.7 | 28.8 | 28.4 |  |  |  |  | 28.4 | 28.6 | 28.5 | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.2 | 33.9 | 33.5 |  |  |  |  | 34.7 | 34 | 34.2 | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 5.1 | 5.1 | 0 | 0 | 0 | 0 | 6.3 | 5.4 | 5.7 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1265.6 | 1303.82 | 1304.3 |  |  |  |  | 1110.2 | 1239.4 | 1291 | 1261.9
| HEAT CAPACITY | kW | 8226.9 | 0 | 8037.8753 | 7678.3857 | 7681.2125 | 0 | 0 | 0 | 0 | 8076.5127 | 7728.3603 | 8497.3441 | 8305.8083
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.46 | 0.46 |  |  |  |  | 0.47 | 0.48 | 0.46 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.8 | 19.7 | 19.8 |  |  |  |  | 20.1 | 20.8 | 19.8 | 20
| LIQUID LEVEL | mm | mm |  | 187.8 | 124.6 | 124.6 |  |  |  |  | 160.5 | 214.1 | 198 | 204.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.52 | 4.71 | 4.96 |  |  |  |  | 4.69 | 5.2 | 4.79 | 5.09
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 2
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  |  | OK | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 68.6 | 78 |  | 78 |  |  | 73.5 | 73.5 |  | 74.1 | 75.5 | 75.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.3 | 0 |  | 0 |  |  | 0.2 | 0.2 |  | 0 | 0.2 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% | 62.7 | 73.2 |  | 73.2 |  |  | 67.7 | 67.7 |  | 68.9 | 70 | 70
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 70.2 | 69.4 |  | 69.4 |  |  | 69.8 | 67.8 |  | 75.6 | 72.3 | 75
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 73.8 | 47.4 |  | 47.4 |  |  | 32.2 | 34.6 |  | 48 | 41.4 | 38.3
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  |  | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 117.3 | 118.2 |  | 117 |  |  | 115.9 | 116.4 |  | 117.1 | 114.6 | 115.6
| INPUT | Kw | 1194kW | 1153 | 1155 |  | 1207 |  |  | 1193 | 1198 |  | 1210 | 1177 | 1188
COMPRESSOR | RUNNING TIME | Hr | NA | 46109.3 | [5 empty] | 46912.2 |  |  |  | 48030.6 | 48022
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 58 |  | 59.3 |  |  | 57.2 | 57.3 |  | 58.8 | 59.4 | 59.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 |  | 0.5 |  |  | 0.53 | 0.53 |  | 0.48 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.7 | 45.1 |  | 44.7 |  |  | 45.3 | 45.1 |  | 44.9 | 45.6 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.24 | 0.23 |  | 0.22 |  |  | 0.23 | 0.22 |  | 0.23 | 0.22 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 5.4 | 4.3 |  | 4.1 |  |  | 4.5 | 4.4 |  | 4.8 | 4.1 | 4.3
| SATURATION TEMPERATURE | CELCIUS | C | 4.8 | 3.9 |  | 3.1 |  |  | 3.3 | 3.4 |  | 3.3 | 3.3 | 3.4
| APPROACH TEMP | CELCIUS | C |  | 1.1 |  | 2.2 | 0 | 0 | 1.4 | 1.3 | 0 | 1.6 | 1.4 | 1.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 736.8 | 728.4 |  | 735.5 |  |  | 617.5 | 663.7 |  | 740.1 | 629.5 | 629.3
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.9 | 13 |  | 14 |  |  | 14.1 | 13.5 |  | 13.9 | 13.2 | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5.9 | 5 |  | 5.3 |  |  | 4.7 | 4.7 |  | 4.9 | 4.7 | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8 | 8 | 0 | 8.7 | 0 | 0 | 9.4 | 8.8 | 0 | 9 | 8.5 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 6806.4665 | 6728.8684 | 0 | 7388.9723 | 0 | 0 | 6702.6559 | 6744.2956 | 0 | 7691.5704 | 6178.6952 | 6176.7321
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.88 | 0.82 |  | 0.87 |  |  | 0.85 | 0.88 |  | 0.86 | 0.82 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.6 | 36 |  | 37.7 |  |  | 38 | 38.1 |  | 37.2 | 36.5 | 36.9
| SATURATED TEMEPRATURE | CELCIUS | C | 37.5 | 36.4 |  | 38.5 |  |  | 37.9 | 38 |  | 37.7 | 36.6 | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.8 | 2.1 | 0 | 4.3 | 0 | 0 | 3.4 | 3.3 | 0 | 2.4 | 2.2 | 2.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.1 | 38.7 |  | 29.4 |  |  | 29.1 | 29.3 |  | 29.1 | 28.8 | 29.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.7 | 34.3 |  | 34.2 |  |  | 34.5 | 34.7 |  | 35.3 | 34.4 | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | -4.4 | 0 | 4.8 | 0 | 0 | 5.4 | 5.4 | 0 | 6.2 | 5.6 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1227 | 1259.4 |  | 1298.8 |  |  | 1214 | 1245.6 |  | 1086.5 | 1233.9 | 1264.2
| HEAT CAPACITY | kW | 8226.9 | 7934.4111 | -6398.7991 | 0 | 7198.8915 | 0 | 0 | 7569.9769 | 7767.0208 | 0 | 7778.6374 | 7979.03 | 8466.9284
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.48 | 0.46 |  | 0.48 |  |  | 0.48 | 0.48 |  | 0.48 | 0.47 | 0.48
| SATURATED TEMPERATURE | CELCIUS | C | 20.9 | 19.6 |  | 20.3 |  |  | 20.8 | 20.9 |  | 20.5 | 20.2 | 20.4
| LIQUID LEVEL | mm | mm | 200.3 | 168.5 |  | 134.5 |  |  | 202.1 | 198.7 |  | 147.7 | 191.4 | 205.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.35 | 5.22 |  | 5.13 |  |  | 5.82 | 5.4 |  | 5.55 | 5.45 | 5.32
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 3
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK |  |  | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.1 | 77 | 74.8 |  |  | 71.9 | 72.2 | 72.9 | 73.5 |  | 75.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0.2 | 0 |  |  | 0.1 | 0.1 | 0 | 0 |  | 0.3
OPENING OF 2nd VANE |  | % | 0~100% |  | 67.1 | 72.1 | 69.6 |  |  | 68.2 | 67.5 | 67.3 | 67.8 |  | 71
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 64.1 | 70.6 | 67.7 |  |  | 64.9 | 65.6 | 70.7 | 71.7 |  | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 55.3 | 48.6 | 50.1 |  |  | 42.1 | 35.3 | 68.1 | 67.8 |  | 40
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  |  | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 114.9 | 117.4 | 115.8 |  |  | 117.9 | 118.2 | 118.6 | 119.1 |  | 118
| INPUT | Kw | 1194kW |  | 1150 | 1197 | 1179 |  |  | 1201 | 1200 | 1201 | 1208 |  | 1199
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46060 |  | 46844 |  |  |  | 46861 |  | 46128 |  | 47972
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 57.8 | 59.3 | 58.8 |  |  | 58.1 | 57.2 | 58.5 | 58.9 |  | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.5 | 0.5 |  |  | 0.53 | 0.54 | 0.48 | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 | 44.7 | 45 |  |  | 45 | 45 | 44.8 | 44.9 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.22 | 0.22 |  |  | 0.22 | 0.23 | 0.22 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 | 4.1 | 4 |  |  | 4.5 | 4.6 | 4.8 | 4.9 |  | 4.4
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 | 3.1 | 3.2 |  |  | 3.4 | 3.7 | 3.6 | 3.5 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 1.3 | 3.2 | 0 | 0 | 1.7 | 1.3 | 0.1 | 1.5 | 0 | 1.6
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 723.44 | 669.2 | 704.24 |  |  | 713.6 | 721.68 | 701.8 | 728 |  | 705.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13 | 12.9 | 13.1 |  |  | 12.9 | 13.5 | 12.9 | 13.2 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 | 5.4 | 6.4 |  |  | 5.1 | 5 | 4.9 | 5 |  | 5.4
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8 | 7.5 | 6.7 | 0 | 0 | 7.8 | 8.5 | 8 | 8.2 | 0 | 7.9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6683.0485 | 5795.612 | 5448.5081 | 0 | 0 | 6427.3441 | 7083.4642 | 6483.1409 | 6893.3025 | 0 | 6436.7667
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.86 | 0.86 |  |  | 0.85 | 0.85 | 0.81 | 0.81 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.1 | 37.4 | 37.1 |  |  | 38 | 37.5 | 36.8 | 36.9 |  | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 | 38.2 | 38 |  |  | 37.6 | 37.6 | 37.5 | 37.3 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.2 | 4.3 | 4.3 | 0 | 0 | 3.6 | 3.4 | 3.4 | 2.4 | 0 | 0.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.7 | 28 | 29 |  |  | 28.1 | 28.7 | 27.9 | 28.7 |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.2 | 33.9 | 33.7 |  |  | 34 | 34.2 | 34.1 | 34.9 |  | 36.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 5.9 | 4.7 | 0 | 0 | 5.9 | 5.5 | 6.2 | 6.2 | 0 | 7.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1265 | 1249.9 | 1300.6 |  |  | 1221.1 | 1243.06 | 1101.2 | 1087.24 |  | 1263.64
| HEAT CAPACITY | kW | 8226.9 | 0 | 8034.0647 | 8515.485 | 7058.6836 | 0 | 0 | 8319.2725 | 7894.7229 | 7883.8799 | 7783.9353 | 0 | 11527.4319
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.47 | 0.47 |  |  | 0.48 | 0.48 | 0.47 | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.8 | 20.3 | 20.2 |  |  | 19.9 | 20 | 19.9 | 20.4 |  | 20.2
| LIQUID LEVEL | mm | mm |  | 187.8 | 124.7 | 128.8 |  |  | 211.1 | 201 | 149.9 | 159.8 |  | 198.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.52 | 5.11 | 5.12 |  |  | 5.05 | 5 | 4.86 | 4.98 |  | 4.82
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 4
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  |  |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 73.9 | 70.8 |  | 80.4 |  |  |  | 73.5 | 77 | 70.9 | 80.1 | 74.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.3 | 0.3 |  | 0.1 |  |  |  | 0.2 | 0 | 0 | 0.2 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% | 68.3 | 65.4 |  | 76.2 |  |  |  | 67.7 | 72.7 | 64.4 | 76.6 | 69.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 66 | 66.2 |  | 67.9 |  |  |  | 68.3 | 72.3 | 72.2 | 73.4 | 74.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 80 | 70 |  | 50.3 |  |  |  | 33.3 | 56.2 | 64.4 | 48.1 | 41.1
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  |  |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 116.9 | 119.1 |  | 121 |  |  |  | 120.2 | 118.6 | 119.4 | 118 | 119.8
| INPUT | Kw | 1194kW | 1151 | 1171 |  | 1219 |  |  |  | 1219 | 1215 | 1205 | 1205 | 1208
COMPRESSOR | RUNNING TIME | Hr | NA | 46143.2 | 46134.8 |  | 46933.6 |  |  |  | 46951.5 | 46232 | 46223.1 | 48064.7 | 48055.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.5 | 58.2 |  | 59.4 |  |  |  | 57.4 | 58.5 | 58.9 | 59.1 | 59.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.51 |  |  |  | 0.54 | 0.48 | 0.48 | 0.47 | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 44.9 |  | 45.1 |  |  |  | 45 | 44.9 | 44.9 | 45 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.24 |  | 0.22 |  |  |  | 0.23 | 0.23 | 0.24 | 0.22 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.3 | 4.7 |  | 3.7 |  |  |  | 5 | 4.6 | 5.4 | 4 | 4.9
| SATURATION TEMPERATURE | CELCIUS | C | 3.6 | 4.4 |  | 2.9 |  |  |  | 3.9 | 3.6 | 4 | 3.7 | 4
| APPROACH TEMP | CELCIUS | C | 1.2 | 0.9 | 0 | 2.4 | 0 | 0 | 0 | 1.4 | 0.3 | 1.6 | 1.3 | 1.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 745.7 | 731 |  | 705.7 |  |  |  | 714.7 | 759.7 | 740.8 | 732.1 | 705.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.9 | 13.5 |  | 13.6 |  |  |  | 13.5 | 13 | 13.6 | 13.1 | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.8 | 5.3 |  | 5.3 |  |  |  | 5.3 | 4.9 | 5.6 | 5 | 5.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.1 | 8.2 | 0 | 8.3 | 0 | 0 | 0 | 8.2 | 8.1 | 8 | 8.1 | 7.9
| CHILLING CAPACITY | kW | 7032.6kW | 6974.7921 | 6921.709 | 0 | 6763.6374 | 0 | 0 | 0 | 6767.3672 | 7105.739 | 6843.418 | 6847.5866 | 6434.9423
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.83 |  | 0.87 |  |  |  | 0.85 | 0.8 | 0.81 | 0.82 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.2 | 36.8 |  | 37.6 |  |  |  | 38.3 | 35.1 | 37.3 | 34.7 | 37.1
| SATURATED TEMEPRATURE | CELCIUS | C | 34.5 | 37.1 |  | 38.6 |  |  |  | 38.2 | 35.6 | 37.7 | 34.9 | 37.1
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2 | 2.1 | 0 | 4.4 | 0 | 0 | 0 | 3.4 | 2.5 | 2.3 | 2.3 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 26.7 | 29.4 |  | 29.4 |  |  |  | 29.2 | 26.8 | 29.1 | 26.8 | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 32.5 | 35 |  | 34.2 |  |  |  | 34.8 | 33.1 | 35.4 | 32.6 | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.8 | 5.6 | 0 | 4.8 | 0 | 0 | 0 | 5.6 | 6.3 | 6.3 | 5.8 | 5.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1293.8 | 1265.5 |  | 1306.4 |  |  |  | 1246.3 | 1114.5 | 1081.1 | 1296.2 | 1265.6
| HEAT CAPACITY | kW | 8226.9 | 8665.1732 | 8183.3718 | 0 | 7241.0162 | 0 | 0 | 0 | 8059.2148 | 8107.7945 | 7864.8152 | 8681.2471 | 8622.448
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.44 | 0.48 |  | 0.47 |  |  |  | 0.49 | 0.45 | 0.49 | 0.45 | 0.48
| SATURATED TEMPERATURE | CELCIUS | C | 18.5 | 20.5 |  | 20.2 |  |  |  | 21.2 | 19.6 | 21.1 | 18.9 | 20.9
| LIQUID LEVEL | mm | mm | 165.3 | 223.5 |  | 128.8 |  |  |  | 211.2 | 154.3 | 162.6 | 197.8 | 202.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.19 | 5.07 |  | 4.94 |  |  |  | 5.06 | 4.95 | 4.82 | 4.99 | 4.88
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 5
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  |  |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 73.9 |  | 77 |  |  |  | 75.9 |  | 76.7 |  | 78
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.3 |  | 0.1 |  |  |  | 0.1 |  | 0 |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 68.4 |  | 72.3 |  |  |  | 71.2 |  | 72.7 |  | 73.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 65.1 |  | 67.3 |  |  |  | 65.8 |  | 71.5 |  | 72.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 84.6 |  | 55.9 |  |  |  | 34.8 |  | 63.7 |  | 44.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  |  |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.6 |  | 118.5 |  |  |  | 119.7 |  | 121.1 |  | 118.6
| INPUT | Kw | 1194kW |  | 1149 |  | 1200 |  |  |  | 1233 |  | 1243 |  | 1216
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46158 |  | 46943 |  |  |  | 46961 |  | 46247 |  | 48074
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 |  | 59 |  |  |  | 57.5 |  | 58.8 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.5 |  |  |  | 0.54 |  | 0.49 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 44.9 |  |  |  | 44.5 |  | 44.6 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 |  |  |  | 0.23 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 3.8 |  | 4 |  |  |  | 4.8 |  | 4.9 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 |  | 2.9 |  |  |  | 3.7 |  | 3.7 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 0 | 2.1 | 0 | 0 | 0 | 1 | 0 | 1.2 | 0 | 1.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 724.24 |  | 695.28 |  |  |  | 719.36 |  | 729.28 |  | 706.72
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.9 |  | 12.9 |  |  |  | 13.3 |  | 13 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 |  | 5 |  |  |  | 4.7 |  | 4.9 |  | 5.4
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.2 | 0 | 7.9 | 0 | 0 | 0 | 8.6 | 0 | 8.1 | 0 | 7.9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6857.6998 | 0 | 6342.6236 | 0 | 0 | 0 | 7143.7598 | 0 | 6821.2102 | 0 | 6446.9838
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.86 |  |  |  | 0.85 |  | 0.84 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.1 |  | 36.9 |  |  |  | 37.8 |  | 36.7 |  | 36.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.5 |  | 37.8 |  |  |  | 37.7 |  | 37.2 |  | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.9 | 0 | 4.9 | 0 | 0 | 0 | 4.3 | 0 | 3.2 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.2 |  | 27.9 |  |  |  | 27.8 |  | 27.9 |  | 28.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.6 |  | 32.9 |  |  |  | 33.4 |  | 34 |  | 33.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.4 | 0 | 5 | 0 | 0 | 0 | 5.6 | 0 | 6.1 | 0 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1263.36 |  | 1302 |  |  |  | 1244.18 |  | 1086.4 |  | 1261.12
| HEAT CAPACITY | kW | 8226.9 | 0 | 7877.7644 | 0 | 7517.321 | 0 | 0 | 0 | 8045.5058 | 0 | 7652.4711 | 0 | 8009.4226
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.42 |  |  |  | 0.45 |  | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.7 |  | 20 |  |  |  | 21.2 |  | 20 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 310.5 |  | 120.1 |  |  |  | 210.2 |  | 164.7 |  | 201.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.39 |  | 4.98 |  |  |  | 4.93 |  | 4.86 |  | 5
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 6
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  |  |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 68.6 | 72.4 | 78 | 77 |  |  |  | 76.7 | 74.1 | 76.7 |  | 78.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.3 | 0.8 | 0 | 0.1 |  |  |  | 0 | 0 | 0 |  | 0.3
OPENING OF 2nd VANE |  | % | 0~100% | 62.7 | 66.1 | 73.2 | 72.3 |  |  |  | 71.1 | 68.9 | 71.1 |  | 74.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 70.2 | 64.9 | 69.4 | 67.3 |  |  |  | 71 | 75.6 | 71.1 |  | 71.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 73.8 | 52 | 47.4 | 55.9 |  |  |  | 34.8 | 48 | 63.7 |  | 42.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 |  |  |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 117.3 | 117.4 | 117 | 117.8 |  |  |  | 120.9 | 117.1 | 121.1 |  | 119.4
| INPUT | Kw | 1194kW | 1153 | 1157 | 1207 | 1199 |  |  |  | 1227 | 1210 | 1243 |  | 1208
COMPRESSOR | RUNNING TIME | Hr | NA | 46178.7 | 46167.9 | 46978 | 46967.2 |  |  |  | 46256.8 | 46267.6 | 46256.8 |  | 48092.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 58.5 | 59.3 | 59 |  |  |  | 44.8 | 58.8 | 58.8 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 | 0.5 | 0.5 |  |  |  | 0.54 | 0.48 | 0.49 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.7 | 44.9 | 44.7 | 44.9 |  |  |  | 44.8 | 44.9 | 44.8 |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.24 | 0.28 | 0.22 | 0.22 |  |  |  | 0.2 | 0.23 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 5.4 | 4.5 | 4.1 | 3.4 |  |  |  | 4.7 | 4.8 | 4.7 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C | 4.8 | 3.9 | 3.1 | 2.5 |  |  |  | 3.7 | 3.3 | 3.7 |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0.2 | 0.7 | 1.2 | 2.1 | 0 | 0 | 0 | 0.8 | 0.1 | 0.7 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 728.4 | 727.36 | 735.5 | 695.28 |  |  |  | 719.76 | 740.1 | 729.04 |  | 705.36
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13 | 12.5 | 14 | 12.6 |  |  |  | 12.8 | 13.9 | 12.5 |  | 12.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5 | 4.6 | 5.3 | 4.6 |  |  |  | 4.5 | 4.9 | 4.4 |  | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8 | 7.9 | 8.7 | 8 | 0 | 0 | 0 | 8.3 | 9 | 8.1 | 0 | 7.9
| CHILLING CAPACITY | kW | 7032.6kW | 6728.8684 | 6635.2702 | 7388.9723 | 6422.9099 | 0 | 0 | 0 | 6898.3926 | 7691.5704 | 6818.9654 | 0 | 6434.5774
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.81 | 0.87 | 0.84 |  |  |  | 0.83 | 0.86 | 0.82 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36 | 35.6 | 37.7 | 36.9 |  |  |  | 37.8 | 37.2 | 36.7 |  | 36.4
| SATURATED TEMEPRATURE | CELCIUS | C | 36.4 | 35.9 | 38.5 | 37.4 |  |  |  | 37 | 37.7 | 36.6 |  | 36
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.1 | 2.7 | 4.3 | 4.8 | 0 | 0 | 0 | 4.3 | 2.4 | 3.2 | 0 | 8.5
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.7 | 27.7 | 29.4 | 27.6 |  |  |  | 27.2 | 29.1 | 27.3 |  | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.3 | 33.2 | 34.2 | 32.6 |  |  |  | 32.7 | 35.3 | 33.4 |  | 27.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 5.5 | 4.8 | 5 | 0 | 0 | 0 | 5.5 | 6.2 | 6.1 | 0 | 0
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1259.4 | 1260.84 | 1298.8 | 1299.36 |  |  |  | 1245.44 | 1086.5 | 1086.4 |  | 1261.12
| HEAT CAPACITY | kW | 8226.9 | 8143.9261 | 8007.6443 | 7198.8915 | 7502.0785 | 0 | 0 | 0 | 7909.8383 | 7778.6374 | 7652.4711 | 0 | 0
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.46 | 0.48 | 0.42 |  |  |  | 0.46 | 0.48 | 0.46 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 19.6 | 19.5 | 20.3 | 19.3 |  |  |  | 19.7 | 20.5 | 19.7 |  | 19.7
| LIQUID LEVEL | mm | mm | 168.5 | 172.9 | 134.5 | 122.5 |  |  |  | 210.2 | 147.7 | 168.4 |  | 193.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.22 | 5.13 | 5.13 | 5.11 |  |  |  | 4.93 | 5.55 | 4.85 |  | 4.96
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 7
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK |  |  | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 67.4 |  | 77.2 | 75.2 | 75.2 | 72.5 | 72.5 |  |  | 75.1 | 75.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 1 |  | 0.1 | 0.2 | 0.2 | 0.1 | 0.2 |  |  | 0.3 | 0.3
OPENING OF 2nd VANE |  | % | 0~100% |  | 61.6 |  | 72.8 | 42.2 | 70.4 | 66.6 | 66.6 |  |  | 70.7 | 70.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.9 |  | 69.4 | 63.8 | 63.2 | 70.7 | 66.3 |  |  | 77.4 | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 48.1 |  | 48 | 70.4 | 35.8 | 36.8 | 30.6 |  |  | 45.1 | 37.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  |  | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 114.1 |  | 118.6 | 115.6 | 118.8 | 116.1 | 117.1 |  |  | 114.7 | 118.7
| INPUT | Kw | 1194kW |  | 1142 |  | 1206 | 1189 | 1216 | 1191 | 1200 |  |  | 1172 | 1213
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46192 |  | 46988 | 44578 | 44570 | 47002 | 46993.9 |  |  | 48111 | 48102.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.1 | 57.9 | 57.7 | 57.3 | 57.3 |  |  | 59.3 | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 | 0.5 | 0.59 | 0.53 | 0.54 |  |  | 0.47 | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 |  | 45.2 | 44.9 | 44.9 | 45.1 | 45 |  |  | 45.3 | 44.6
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.21 |  | 0.22 | 0.23 | 0.22 | 0.23 | 0.23 |  |  | 0.23 | 0.21
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.8 |  | 4.1 | 4.1 | 4.3 | 4.7 | 4.8 |  |  | 4 | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.4 |  | 3.3 | 3.5 | 3.4 | 3.3 | 3.7 |  |  | 3.2 | 3.8
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0 | 1.8 | 0.4 | 0.6 | 1 | 1.2 | 0 | 0 | 1.5 | 1.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 730.24 |  | 703.68 | 662.88 | 658.24 | 628.24 | 693.12 |  |  | 660.32 | 714.32
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.9 |  | 13 | 13.5 | 13.6 | 13.7 | 13.4 |  |  | 13.2 | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5.2 |  | 5.1 | 4.5 | 4.9 | 4.3 | 4.9 |  |  | 4.7 | 5.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 7.7 | 0 | 7.9 | 9 | 8.7 | 9.4 | 8.5 | 0 | 0 | 8.5 | 7.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6492.8961 | 0 | 6419.2517 | 6889.0531 | 6612.8037 | 6819.2333 | 6803.1409 | 0 | 0 | 6481.2009 | 6268.8591
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.84 |  | 0.88 | 0.82 | 0.85 | 0.83 | 0.82 |  |  | 0.8 | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 37 |  | 37.8 | 35.4 | 37.2 | 36.8 | 38.7 |  |  | 35.5 | 37.4
| SATURATED TEMEPRATURE | CELCIUS | C |  | 37.2 |  | 38.7 | 36.4 | 37.9 | 36.7 | 38.4 |  |  | 35.7 | 37.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 1.8 | 0 | 4.2 | 3.9 | 2.8 | 4.2 | 4 | 0 | 0 | 2.9 | 2.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.5 |  | 29.5 | 27.2 | 29.5 | 27 | 28.9 |  |  | 27.3 | 29.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 35.4 |  | 34.5 | 32.5 | 35.1 | 32.5 | 34.4 |  |  | 32.8 | 35.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.9 | 0 | 5 | 5.3 | 5.6 | 5.5 | 5.5 | 0 | 0 | 5.5 | 6.1
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1220.3 |  | 1260.56 | 1298.5 | 1293 | 1228.08 | 1201.48 |  |  | 1245.86 | 1218
| HEAT CAPACITY | kW | 8226.9 | 0 | 8313.8222 | 0 | 7278.06 | 7946.94 | 8361.2009 | 7799.5843 | 7630.6467 | 0 | 0 | 7912.5058 | 8579.4457
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 |  | 0.48 | 0.45 | 0.47 | 0.47 | 0.49 |  |  | 0.46 | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.9 |  | 20.6 | 19.1 | 20.1 | 20.1 | 21.3 |  |  | 19.3 | 20.9
| LIQUID LEVEL | mm | mm |  | 219.1 |  | 130.4 | 196.9 | 207.1 | 197.6 | 216.1 |  |  | 189.3 | 212.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.01 |  | 5.01 | 5.59 | 5.31 | 5.69 | 5.28 |  |  | 5.93 | 4.73
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 8
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK |  | OK |  |  | OK | OK
OPENING OF VANE |  | % | 0~100% | 74.3 | 70.2 |  | 73.9 | 75.8 | 73.2 |  | 78.6 |  |  | 78.5 | 78.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0 |  | 0 | 0 | 0 |  | 0.2 |  |  | 0.3 | 0.3
OPENING OF 2nd VANE |  | % | 0~100% | 69 | 64.4 |  | 68.4 | 71.4 | 68.4 |  | 73.7 |  |  | 73.9 | 73.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 63.9 | 68.7 |  | 69.5 | 62.5 | 64.1 |  | 68.1 |  |  | 70.8 | 74.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 52.6 | 50.7 |  | 60.6 | 40.2 | 42.5 |  | 38.4 |  |  | 41.1 | 41.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  |  | 6.6 | 6.6
| CURRENT | A | ≤115A | 118.2 | 115.1 |  | 114.3 | 117.6 | 115.2 |  | 117.7 |  |  | 118.6 | 114.4
| INPUT | Kw | 1194kW | 1164 | 1135 |  | 1164 | 1194 | 1170 |  | 1214 |  |  | 1202 | 1179
COMPRESSOR | RUNNING TIME | Hr | NA | 46210.7 | 46201.8 |  | 46997.9 | 44599.4 | 44590.5 |  | 47017.6 |  |  | 48135.6 | 48126.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.8 | 58.4 |  | 59.2 | 57.7 | 57.4 |  | 57 |  |  | 59.2 | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.5 | 0.58 | 0.58 |  | 0.53 |  |  | 0.48 | 0.47
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.3 | 44.5 |  | 45 | 45.1 | 44.6 |  | 44.6 |  |  | 45.1 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.28 | 0.23 |  | 0.22 | 0.23 | 0.22 |  | 0.22 |  |  | 0.22 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.5 | 4.5 |  | 4.4 | 4 | 4 |  | 4 |  |  | 4.2 | 3.6
| SATURATION TEMPERATURE | CELCIUS | C | 3.8 | 4.2 |  | 3.4 | 3.3 | 3.3 |  | 3.2 |  |  | 3.2 | 2.7
| APPROACH TEMP | CELCIUS | C | 0.5 | 1 | 0 | 2.2 | 1 | 0.8 | 0 | 1.3 | 0 | 0 | 1.6 | 1.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 747.12 | 742.4 |  | 713.2 | 686.96 | 661.52 |  | 647.3 |  |  | 731.92 | 650.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.1 | 13.6 |  | 13.6 | 12.8 | 13 |  | 13.6 |  |  | 12.4 | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 5.2 |  | 5.6 | 4.3 | 4.1 |  | 4.5 |  |  | 4.8 | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.8 | 8.4 | 0 | 8 | 8.5 | 8.9 | 0 | 9.1 | 0 | 0 | 7.6 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 6729.2564 | 7201.1085 | 0 | 6588.4527 | 6742.679 | 6798.5312 | 0 | 6801.8822 | 0 | 0 | 6423.3164 | 6534.0416
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.78 |  | 0.82 | 0.83 | 0.8 |  | 0.81 |  |  | 0.82 | 0.78
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.8 | 34.6 |  | 35.6 | 36 | 34.8 |  | 36.1 |  |  | 36.1 | 35
| SATURATED TEMEPRATURE | CELCIUS | C | 36.2 | 35.1 |  | 36.5 | 36.7 | 35.6 |  | 36.2 |  |  | 36.2 | 35
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.9 | 2 | 0 | 4.4 | 3.7 | 3 | 0 | 3.4 | 0 | 0 | 2.9 | 2.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.8 | 27 |  | 26.9 | 27.5 | 37 |  | 26.9 |  |  | 27.7 | 26.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.3 | 33.1 |  | 32.1 | 33 | 32.6 |  | 32.8 |  |  | 33.3 | 32.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 6.1 | 0 | 5.2 | 5.5 | -4.4 | 0 | 5.9 | 0 | 0 | 5.6 | 6.1
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1214.78 | 1236.5 |  | 1276.2 | 1294.02 | 1297.5 |  | 1219.2 |  |  | 1215.62 | 1237.7
| HEAT CAPACITY | kW | 8226.9 | 7715.1155 | 8709.7575 | 0 | 7663.0947 | 8218.3718 | -6592.3788 | 0 | 8306.3279 | 0 | 0 | 7860.8222 | 8718.2102
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.46 |  | 0.46 | 0.46 | 0.45 |  | 0.46 |  |  | 0.46 | 0.45
| SATURATED TEMPERATURE | CELCIUS | C | 19.3 | 19.4 |  | 19.3 | 19.4 | 18.9 |  | 19.3 |  |  | 19.7 | 18.8
| LIQUID LEVEL | mm | mm | 161.7 | 197.8 |  | 128.4 | 201.7 | 213.7 |  | 218.1 |  |  | 203.8 | 207.4
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.2 | 5.3 |  | 5.06 | 5.28 | 5.62 |  | 5.55 |  |  | 4.7 | 5.47
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 9
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK |  | OK |  |  | OK | OK
OPENING OF VANE |  | % | 0~100% | 73.9 | 69.3 | 78 | 79.4 |  | 74.6 | 76.7 | 72.5 |  |  |  | 71.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.3 | 0.4 | 0 | 0 |  | 0 | 0 | 0.2 |  |  |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% | 68.4 | 63.8 | 73.2 | 75.4 |  | 69.8 | 71.1 | 67.9 |  |  |  | 66.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 65.1 | 66.7 | 69.4 | 68.5 |  | 63.3 | 71 | 67.8 |  |  |  | 74.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 84.6 | 49.9 | 47.4 | 50.3 |  | 39.6 | 34.8 | 35.9 |  |  |  | 39.3
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  |  |  | 6.6
| CURRENT | A | ≤115A | 117.6 | 116.7 | 117 | 118.6 |  | 117.8 | 120.9 | 119.1 |  |  |  | 115.2
| INPUT | Kw | 1194kW | 1149 | 1151 | 1207 | 1205 |  | 1201 | 1227 | 1212 |  |  |  | 1173
COMPRESSOR | RUNNING TIME | Hr | NA | 46158 | 46221.1 | 46978 | 47008.3 |  | 44612.8 | 46256.8 | 47028 |  |  |  | 48148.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.8 | 59.3 | 59.1 |  | 57.8 | 44.8 | 57.3 |  |  |  | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 | 0.5 | 0.49 |  | 0.58 | 0.54 | 0.54 |  |  |  | 0.49
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.7 | 44.8 | 44.7 | 45.2 |  | 44.9 | 44.8 | 44.8 |  |  |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.24 | 0.23 | 0.22 | 0.22 |  | 0.22 | 0.2 | 0.23 |  |  |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 5.4 | 4.8 | 4.1 | 3.7 |  | 4.2 | 4.7 | 4.9 |  |  |  | 4.9
| SATURATION TEMPERATURE | CELCIUS | C | 4.8 | 4.2 | 3.1 | 2.9 |  | 3.4 | 3.7 | 3.9 |  |  |  | 4.2
| APPROACH TEMP | CELCIUS | C | 0.2 | 1 | 2.2 | 2.3 | 0 | 0.8 | 0.8 | 1.3 | 0 | 0 | 0 | 1.4
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 728.4 | 733.5 | 735.5 | 710.3 |  | 645.8 | 719.76 | 728.2 |  |  |  | 712.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13 | 13.1 | 14 | 13.4 |  | 13.1 | 12.8 | 13.3 |  |  |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5 | 5.2 | 5.3 | 5.2 |  | 4.2 | 4.5 | 5.2 |  |  |  | 5.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8 | 7.9 | 8.7 | 8.2 | 0 | 8.9 | 8.3 | 8.1 | 0 | 0 | 0 | 7.8
| CHILLING CAPACITY | kW | 7032.6kW | 6728.8684 | 6691.2818 | 7388.9723 | 6725.7044 | 0 | 6636.9746 | 6898.3926 | 6811.1085 | 0 | 0 | 0 | 6421.0393
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.82 | 0.87 | 0.86 |  | 0.84 | 0.83 | 0.85 |  |  |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36 | 36.4 | 37.7 | 37.1 |  | 36.3 | 37.8 | 37.9 |  |  |  | 36.6
| SATURATED TEMEPRATURE | CELCIUS | C | 36.4 | 36.6 | 38.5 | 38 |  | 37.2 | 37 | 37.9 |  |  |  | 36.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.1 | 1.9 | 4.3 | 4.3 | 0 | 2.9 | 4.3 | 3.4 | 0 | 0 | 0 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.7 | 28.7 | 29.4 | 28.7 |  | 28.7 | 27.2 | 28.7 |  |  |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.3 | 34.7 | 34.2 | 33.7 |  | 34.3 | 32.7 | 34.5 |  |  |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 6 | 4.8 | 5 | 0 | 5.6 | 5.5 | 5.8 | 0 | 0 | 0 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1259.4 | 1221.3 | 1298.8 | 1261.7 |  | 1295.7 | 1245.44 | 1198.8 |  |  |  | 1215.7
| HEAT CAPACITY | kW | 8226.9 | 8143.9261 | 8461.6628 | 7198.8915 | 7284.642 | 0 | 8378.6605 | 7909.8383 | 8028.9145 | 0 | 0 | 0 | 8142.1016
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.47 | 0.48 | 0.47 |  | 0.46 | 0.46 | 0.48 |  |  |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C | 19.6 | 20.3 | 20.3 | 19.9 |  | 19.4 | 19.7 | 20 |  |  |  | 20.6
| LIQUID LEVEL | mm | mm | 168.5 | 212.2 | 134.5 | 125.7 |  | 194.8 | 210.2 | 210.2 |  |  |  | 196.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.22 | 5.16 | 5.13 | 5.08 |  | 5.48 | 4.93 | 4.88 |  |  |  | 4.85
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 10
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK |  | OK |  |  | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 69.9 | 79.4 | 79.4 | 75.9 | 72.9 |  | 72.5 |  |  | 77.3 | 77
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 | 0 | 0 | 0 | 0 |  | 0.2 |  |  | 0.1 | 0.1
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.2 | 75.4 | 75.4 | 72.4 | 67 |  | 67.9 |  |  | 72 | 72
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.7 | 64.8 | 67.9 | 61.6 | 64.3 |  | 66.7 |  |  | 69.4 | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 55.3 | 52.4 | 49.6 | 40 | 37.2 |  | 34.1 |  |  | 42.6 | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  |  | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 118 | 117.4 | 119.6 | 118.2 | 116.6 |  | 119.2 |  |  | 116.9 | 120.3
| INPUT | Kw | 1194kW |  | 1142 | 1194 | 1200 | 1205 | 1175 |  | 1202 |  |  | 1189 | 1217
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46241.5 | 47042.5 | 47031.9 | 44632.7 | 44622.1 |  | 47051.7 |  |  | 48168.2 | 48157.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 | 59.1 | 59.4 | 57.8 | 57.6 |  | 57.3 |  |  | 59.3 | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.49 | 0.49 | 0.59 | 0.58 |  | 0.54 |  |  | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 | 45.1 | 44.7 | 44.9 | 45 |  | 45 |  |  | 44.9 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.21 | 0.21 | 0.22 | 0.28 | 0.23 |  | 0.23 |  |  | 0.22 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.9 | 3.4 | 3.6 | 4.2 | 4.3 |  | 4.6 |  |  | 4.1 | 4.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.4 | 2.5 | 2.8 | 3.4 | 3.6 |  | 3.7 |  |  | 3.1 | 3.8
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 2.5 | 2.5 | 0.8 | 0.7 | 0 | 1.3 | 0 | 0 | 1.8 | 1.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 735.9 | 730.2 | 689.8 | 639.4 | 656.7 |  | 689.5 |  |  | 692.2 | 715.7
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.4 | 12.9 | 13.4 | 12.8 | 13.1 |  | 13.5 |  |  | 12.9 | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5.3 | 5 | 5.3 | 4.2 | 4.3 |  | 5 |  |  | 4.9 | 5.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.1 | 7.9 | 8.1 | 8.6 | 8.8 | 0 |  | 0 | 0 | 8 | 7.9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6883.1293 | 6661.1778 | 6451.94 | 6349.6998 | 6673.164 | 0 | 0 | 0 | 0 | 6394.4573 | 6528.903
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.84 | 0.86 | 0.82 | 0.83 |  | 0.85 |  |  | 0.81 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.2 | 36.5 | 37.1 | 36 | 36.4 |  | 37.7 |  |  | 36 | 36.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.6 | 37.4 | 38 | 36.7 | 37.1 |  | 37.7 |  |  | 36 | 36.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2 | 4.3 | 4.2 | 2.9 | 2.9 | 0 | 3.3 | 0 | 0 | 2.2 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.8 | 28 | 28.6 | 28.1 | 28.7 |  | 28.7 |  |  | 27.8 | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.6 | 33.1 | 33.8 | 33.8 | 34.2 |  | 34.4 |  |  | 33.8 | 34.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.8 | 5.1 | 5.2 | 5.7 | 5.5 | 0 | 5.7 | 0 | 0 | 6 | 6.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1220.3 | 1259.3 | 1265.2 | 1299 | 1294.2 |  | 1197 |  |  | 1205.6 | 1211.8
| HEAT CAPACITY | kW | 8226.9 | 0 | 8172.9099 | 7416.2009 | 7597.0439 | 8550 | 8219.515 | 0 | 7878.6374 | 0 | 0 | 8352.8868 | 8675.7044
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.46 | 0.46 | 0.46 | 0.47 |  | 0.48 |  |  | 0.46 | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 | 19.3 | 19.8 | 19.5 | 20.1 |  | 20.5 |  |  | 19.5 | 20.4
| LIQUID LEVEL | mm | mm |  | 165.8 | 123.5 | 123.1 | 207.6 | 205.4 |  | 211.6 |  |  | 196.2 | 200.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.3 | 4.88 | 4.98 | 5.29 | 5.54 |  | 5.18 |  |  | 5.02 | 4.84
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 11
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK |  |  | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 70.8 | 70.8 |  | 75.2 | 72.6 | 74.6 |  |  | 74 | 74 |  | 77
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 |  | 0.1
OPENING OF 2nd VANE |  | % | 0~100% | 64.9 | 64.8 |  | 70.7 | 70.1 | 70.1 |  |  | 68.3 | 70.1 |  | 72
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 72.1 | 64.8 |  | 66.4 | 61.8 | 62.8 |  |  | 70.3 | 68.3 |  | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 64.9 | 31.7 |  | 70.7 | 39.9 | 40.6 |  |  | 40.9 | 70 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  |  | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 115.4 | 116 |  | 116.4 | 115.9 | 118 |  |  | 118.5 | 120 |  | 120.3
| INPUT | Kw | 1194kW | 1145 | 1141 |  | 1187 | 1204 | 1215 |  |  | 1210 | 1213 |  | 1217
COMPRESSOR | RUNNING TIME | Hr | NA | 46262.5 | 46250.4 |  | 47053.6 | 44652.5 | 44640.4 |  |  | 46284.6 | 46272.6 |  | 48180.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.4 |  | 57 | 57.8 | 58 |  |  | 58.7 | 58.8 |  | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.5 | 0.54 | 0.53 |  |  | 0.49 | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 45.1 |  | 45 | 44.9 | 45 |  |  | 44.9 | 44.8 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.21 |  | 0.22 | 0.22 | 0.23 |  |  | 0.23 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.5 | 4.9 |  | 3.6 | 4.7 | 4.3 |  |  | 4.9 | 4.7 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 4.3 | 4.4 |  | 2.8 | 3.9 | 3.6 |  |  | 3.9 | 3.7 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0.7 | 0.9 | 0 | 2.5 | 0.6 | 0.7 | 0 | 0 | 1.3 | 0.7 | 0 | 1.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 752.6 | 645 |  | 689.8 | 660.2 | 656.7 |  |  | 760.6 | 653 |  | 715.7
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.1 | 13.4 |  | 13.4 | 13 | 13.1 |  |  | 13 | 13.4 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5 | 5.3 |  | 5.3 | 4.5 | 4.3 |  |  | 5.2 | 4.4 |  | 5.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.1 | 8.1 | 0 | 8.1 | 8.5 | 8.8 | 0 |  | 7.8 | 9 | 0 | 7.9
| CHILLING CAPACITY | kW | 7032.6kW | 7039.3303 | 6032.9099 | 0 | 6451.94 | 6480.0231 | 6673.164 | 0 | 0 | 6850.6697 | 6786.3741 | 0 | 6528.903
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.82 |  | 0.86 | 0.84 | 0.83 |  |  | 0.83 | 0.82 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.1 | 36.2 |  | 37.1 | 36.6 | 36.4 |  |  | 36.7 | 36.5 |  | 36.8
| SATURATED TEMEPRATURE | CELCIUS | C | 36.5 | 36.6 |  | 38 | 37.3 | 37.1 |  |  | 37 | 36.4 |  | 36.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.1 | 2 | 0 | 4.2 | 2.8 | 2.9 | 0 | 0 | 2.2 | 1.9 | 0 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.9 | 28.8 |  | 28.6 | 28.9 | 28.7 |  |  | 28.7 | 28.7 |  | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.4 | 34.6 |  | 33.8 | 34.5 | 34.2 |  |  | 34.8 | 34.5 |  | 34.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.8 | 0 | 5.2 | 5.6 | 5.5 | 0 | 0 | 6.1 | 5.8 | 0 | 6.2
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1296.2 | 1220.3 |  | 1265.2 | 1289.9 | 1294.2 |  |  | 1151.6 | 1191.2 |  | 1211.8
| HEAT CAPACITY | kW | 8226.9 | 8232.2171 | 8172.9099 | 0 | 7597.0439 | 8341.1547 | 8219.515 | 0 | 0 | 8111.7321 | 7978.0139 | 0 | 8675.7044
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.47 |  | 0.46 | 0.47 | 0.47 |  |  | 0.47 | 0.48 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C | 20.1 | 20.2 |  | 19.8 | 20 | 20.1 |  |  | 20.1 | 20.5 |  | 20.4
| LIQUID LEVEL | mm | mm | 212.2 | 165.8 |  | 123.1 | 211.3 | 205.4 |  |  | 153.4 | 201 |  | 200.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.19 | 5.34 |  | 5.07 | 5.2 | 5.25 |  |  | 4.73 | 4.82 |  | 5.34
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 12
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK |  |  |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 73.5 | 73.2 | 75.9 | 76 | 75.4 |  |  |  | 73.1 | 80.1 | 78.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0.2 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 68.2 | 69.6 | 71.3 | 71.7 | 69 |  |  |  | 67.4 | 76.7 | 73.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.9 | 68.9 | 71.4 | 65 | 69.6 |  |  |  | 76 | 73.9 | 74
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 56.9 | 62.4 | 56.2 | 42.7 | 39.3 |  |  |  | 50.7 | 46.5 | 45.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  |  | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 118.2 | 113 | 117.2 | 116.4 | 117.8 |  |  |  | 117.5 | 118 | 118.1
| INPUT | Kw | 1194kW |  | 1159 | 1153 | 1186 | 1194 | 1191 |  |  |  | 1187 | 1204 | 1192
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46271.9 | 47072.6 | 47063.3 | 44667.4 | 44658.1 |  |  |  | 46296.4 | 48199.8 | 48190.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 | 58.9 | 59 | 57.7 | 58 |  |  |  | 58.6 | 59.2 | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.5 | 0.58 | 0.59 |  |  |  | 0.48 | 0.47 | 0.47
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 | 45.1 | 45 | 45.1 | 44.9 |  |  |  | 44.9 | 44.8 | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.26 | 0.22 | 0.22 | 0.22 | 0.26 |  |  |  | 0.23 | 0.22 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 | 4 | 3.6 | 4.3 | 4.2 |  |  |  | 3.9 | 4 | 3.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.6 | 3.1 | 2.7 | 3.3 | 3.2 |  |  |  | 2.8 | 3.1 | 2.7
| APPROACH TEMP | CELCIUS | C | 0 | 1 | 2.2 | 2.1 | 0.9 | 0.8 | 0 | 0 | 0 | 1.2 | 1.8 | 1.4
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 646.4 | 729 | 638.9 | 674.4 | 648.6 |  |  |  | 636.4 | 701.5 | 647.4
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.7 | 13.2 | 13.7 | 13 | 12.9 |  |  |  | 13.2 | 13.1 | 12.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 | 5.3 | 4.8 | 4.2 | 4 |  |  |  | 4 | 4.9 | 4.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 9.1 | 7.9 | 8.9 | 8.8 | 8.9 | 0 |  | 0 | 9.2 | 8.2 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6792.4249 | 6650.2309 | 6566.0624 | 6853.0254 | 6665.7506 | 0 | 0 | 0 | 6760.8314 | 6642.3788 | 6429.1455
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.82 | 0.85 | 0.8 | 0.83 |  |  |  | 0.83 | 0.79 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36 | 35.5 | 36.9 | 34.8 | 36.4 |  |  |  | 36.5 | 35.1 | 36.1
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 | 36.4 | 37.9 | 35.7 | 37.1 |  |  |  | 36.7 | 35.2 | 36.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.1 | 4.4 | 4.4 | 2.9 | 2.9 | 0 | 0 | 0 | 2.9 | 2.3 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.7 | 27 | 28.6 | 27.1 | 28.7 |  |  |  | 28.5 | 26.8 | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.3 | 32 | 33.5 | 32.8 | 34.2 |  |  |  | 33.8 | 32.9 | 34
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.6 | 5 | 4.9 | 5.7 | 5.5 | 0 | 0 | 0 | 5.3 | 6.1 | 5.6
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1269.9 | 1259.6 | 1291.8 | 1299.9 | 1291.1 |  |  |  | 1093.1 | 1213.1 | 1274.8
| HEAT CAPACITY | kW | 8226.9 | 0 | 8211.8245 | 7272.5173 | 7309.261 | 8555.9238 | 8199.8268 | 0 | 0 | 0 | 6689.873 | 8544.9307 | 8243.5104
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.45 | 0.47 | 0.45 | 0.46 |  |  |  | 0.46 | 0.45 | 0.45
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.7 | 19 | 20.1 | 19 | 19.5 |  |  |  | 19.4 | 19 | 19.2
| LIQUID LEVEL | mm | mm |  | 197.1 | 118 | 133 | 195.9 | 211.5 |  |  |  | 161.6 | 188 | 193.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.86 | 5.09 | 5.41 | 5.47 | 5.55 |  |  |  | 5.71 | 5.05 | 5.5
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 13
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  |  |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.7 |  | 76 |  | 74.6 |  |  |  | 71.8 |  | 80.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.3 |  | 0.4 |  | 0 |  |  |  | 0 |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.1 |  | 70.8 |  | 69 |  |  |  | 65.9 |  | 76.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 65.9 |  | 68.4 |  | 63.3 |  |  |  | 72.3 |  | 72.8
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 42.8 |  | 52.9 |  | 39.6 |  |  |  | 56.1 |  | 43.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  |  |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 118.5 |  | 117.8 |  | 117.5 |  |  |  | 116.5 |  | 119
| INPUT | Kw | 1194kW |  | 1163 |  | 1189 |  | 1200 |  |  |  | 1205 |  | 1226
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46282 |  | 47082 |  | 44682 |  |  |  | 46307 |  | 48215
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59 |  | 57.9 |  |  |  | 58.7 |  | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 |  | 0.59 |  |  |  | 0.5 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.7 |  | 45.1 |  | 44.9 |  |  |  | 45.1 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.24 |  | 0.22 |  | 0.23 |  |  |  | 0.24 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 5 |  | 4 |  | 4.4 |  |  |  | 5.2 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.2 |  | 2.9 |  | 3.5 |  |  |  | 4 |  | 3.1
| APPROACH TEMP | CELCIUS | C | 0 | 0.8 | 0 | 2.2 | 0 | 1.1 | 0 | 0 | 0 | 1 | 0 | 1.6
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 731.2 |  | 680.64 |  | 654.72 |  |  |  | 716.64 |  | 652.08
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.9 |  | 13 |  | 13.5 |  |  |  | 13.1 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 |  | 5.1 |  | 4.6 |  |  |  | 5 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 7.9 | 0 | 7.9 | 0 | 8.9 | 0 |  | 0 | 8.1 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6670.3002 | 0 | 6209.0716 | 0 | 6728.6467 | 0 | 0 | 0 | 6702.9838 | 0 | 6400.3233
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 |  | 0.85 |  | 0.84 |  |  |  | 0.84 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.6 |  | 37.2 |  | 36.8 |  |  |  | 37 |  | 36.9
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 |  | 37.7 |  | 37.2 |  |  |  | 37 |  | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.8 | 0 | 4.8 | 0 | 3.7 | 0 | 0 | 0 | 3.2 | 0 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.3 |  | 28 |  | 28.1 |  |  |  | 27.9 |  | 28.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.6 |  | 32.9 |  | 33.5 |  |  |  | 33.8 |  | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 0 | 4.9 | 0 | 5.4 | 0 | 0 | 0 | 5.9 | 0 | 5.4
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1267.28 |  | 1301.72 |  | 1292.9 |  |  |  | 1086.68 |  | 1269.24
| HEAT CAPACITY | kW | 8226.9 | 0 | 7755.8707 | 0 | 7365.3903 | 0 | 8061.963 | 0 | 0 | 0 | 7403.4781 | 0 | 7914.4296
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.47 |  | 0.46 |  |  |  | 0.48 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.7 |  | 20.2 |  | 20.1 |  |  |  | 20.5 |  | 19.9
| LIQUID LEVEL | mm | mm |  | 175.1 |  | 122.5 |  | 204.9 |  |  |  | 158.1 |  | 201.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.27 |  | 5.17 |  | 5.44 |  |  |  | 5.08 |  | 5.26
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 14
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK |  |  |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 70.1 | 80.6 | 79.7 | 63.4 | 75.2 |  |  |  | 77.1 | 77.9 | 77.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0.2 | 0.4 | 0 | 0 |  |  |  | 0 | 0.3 | 0.3
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.8 | 77.7 | 75.4 | 57.5 | 70.9 |  |  |  | 71.9 | 72.8 | 72.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.2 | 61.9 | 66.5 | 59.6 | 63.1 |  |  |  | 70.3 | 67.4 | 72.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 45.3 | 51.4 | 51.7 | 35 | 37.3 |  |  |  | 56.1 | 39.1 | 43.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  |  |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 116.3 | 116.7 | 117 | 107.3 | 118.1 |  |  |  | 117.8 | 115.5 | 117.2
| INPUT | Kw | 1194kW |  | 1151 | 1187 | 1203 | 1098 | 1213 |  |  |  | 1219 | 1175 | 1209
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46300.2 | 47115.6 | 47105.6 | 44702.1 | 44692.1 |  |  |  | 46330.5 | 48234.6 | 48224.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 | 58.7 | 59.2 | 57.9 | 57.7 |  |  |  | 58.6 | 59.2 | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.48 | 0.49 | 0.59 | 0.59 |  |  |  | 0.5 | 0.47 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 | 45.1 | 45.1 | 45.1 | 44.9 |  |  |  | 45 | 45 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.24 | 0.21 | 0.22 | 0.23 | 0.23 |  |  |  | 0.24 | 0.23 | 0.24
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.8 | 2.9 | 3.5 | 4.3 | 4.2 |  |  |  | 4.2 | 3.5 | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.4 | 2 | 2.7 | 3.4 | 3.6 |  |  |  | 3.7 | 2.3 | 3.4
| APPROACH TEMP | CELCIUS | C | 0 | 0.6 | 1.9 | 1.9 | 0.7 | 0.9 | 0 | 0 | 0 | 0.4 | 1.9 | 1.5
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 730.96 | 678.3 | 661.92 | 671.1 | 655.76 |  |  |  | 638.56 | 674.3 | 658.8
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.8 | 12.2 | 12.8 | 12.1 | 13.2 |  |  |  | 12.9 | 12.4 | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 | 3.9 | 4.6 | 4.1 | 4.5 |  |  |  | 4.1 | 4.2 | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 7.8 | 8.3 | 8.2 | 8 | 8.7 | 0 |  | 0 | 8.8 | 8.2 | 8.3
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6583.7044 | 6501.0277 | 6267.6028 | 6199.5381 | 6587.8891 | 0 | 0 | 0 | 6488.8314 | 6384.8268 | 6314.1339
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.84 | 0.87 | 0.81 | 0.85 |  |  |  | 0.85 | 0.83 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.5 | 36.5 | 37.3 | 35.4 | 36.9 |  |  |  | 37 | 35.9 | 36.9
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.9 | 37.4 | 38.3 | 36.1 | 37.6 |  |  |  | 37.5 | 36 | 36.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.9 | 4.3 | 4.7 | 2.8 | 3.6 | 0 | 0 | 0 | 3.1 | 2.2 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.7 | 28.1 | 28.6 | 28.3 | 28.6 |  |  |  | 28.6 | 28 | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34 | 33.1 | 33.6 | 33.3 | 34 |  |  |  | 34.4 | 33.8 | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 5 | 5 | 5 | 5.4 | 0 | 0 | 0 | 5.8 | 5.8 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1266.58 | 1250.2 | 1302.28 | 1294.7 | 1299.9 |  |  |  | 1089.48 | 1214.4 | 1267.56
| HEAT CAPACITY | kW | 8226.9 | 0 | 7751.5866 | 7218.2448 | 7518.9376 | 7475.1732 | 8105.612 | 0 | 0 | 0 | 7296.7483 | 8133.3949 | 7757.5843
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.45 | 0.47 | 0.46 | 0.47 |  |  |  | 0.24 | 0.46 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.3 | 18.9 | 19.9 | 19.7 | 20.1 |  |  |  | 20 | 19.4 | 20.3
| LIQUID LEVEL | mm | mm |  | 178.6 | 116 | 122.4 | 216.4 | 213.9 |  |  |  | 163.1 | 196.7 | 193.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.22 | 5.2 | 5.27 | 5.42 | 5.39 |  |  |  | 5.51 | 5.17 | 5.17
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 15
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK | OK | OK |  |  | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 72.6 | 72.6 |  | 76.4 | 74.7 | 74.6 |  |  | 76.7 | 76.8 |  | 78
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.3 | 0.3 |  | 0 | 0 | 0 |  |  | 0 | 0 |  | 0.3
OPENING OF 2nd VANE |  | % | 0~100% | 67.4 | 67.4 |  | 71.6 | 68.8 | 68.8 |  |  | 72.1 | 71.4 |  | 73.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 70.6 | 64.8 |  | 67.3 | 63.8 | 62.6 |  |  | 74.1 | 71.2 |  | 72.8
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 63.9 | 69 |  | 48.4 | 40.3 | 37.1 |  |  | 68.3 | 49.1 |  | 42.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  |  | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118.8 | 119.9 |  | 117.4 | 117.8 | 117.8 |  |  | 118.8 | 162.6 |  | 119.3
| INPUT | Kw | 1194kW | 1165 | 1176 |  | 1191 | 1189 | 1202 |  |  | 1213 | 1227 |  | 1213
COMPRESSOR | RUNNING TIME | Hr | NA | 46318 | 46309.8 |  | 47127.9 | 44724 | 44715.9 |  |  | 46349 | 46340.2 |  | 48248.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.4 | 58.2 |  | 59.1 | 57.9 | 57.9 |  |  | 58.6 | 58.7 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.5 | 0.59 | 0.59 |  |  | 0.46 | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.2 | 44.7 |  | 44.8 | 44.9 | 44.8 |  |  | 45 | 44.9 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.21 |  | 0.22 | 0.23 | 0.23 |  |  | 0.23 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.6 | 4.9 |  | 3.9 | 4.2 | 4.6 |  |  | 4.3 | 4.3 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C | 3.9 | 4.3 |  | 3 | 3.7 | 3.7 |  |  | 3.3 | 3.2 |  | 3.1
| APPROACH TEMP | CELCIUS | C | 0.8 | 0.8 | 0 | 1.9 | 1.1 | 0.9 | 0 | 0 | 1 | 1.1 | 0 | 2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 677.92 | 737.36 |  | 662.08 | 663.68 | 650.24 |  |  | 649.84 | 654.16 |  | 665.2
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.4 | 13.1 |  | 13.2 | 13.5 | 13.4 |  |  | 13.2 | 13.2 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.7 | 5.1 |  | 4.9 | 4.8 | 4.6 |  |  | 4.3 | 4.3 |  | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.7 | 8 | 0 | 8.3 | 8.7 | 8.8 | 0 |  | 8.9 | 8.9 | 0 | 8.3
| CHILLING CAPACITY | kW | 7032.6kW | 6810.5127 | 6811.6397 | 0 | 6345.5704 | 6667.455 | 6607.5196 | 0 | 0 | 6678.4942 | 6722.8915 | 0 | 6375.4734
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.83 |  | 0.86 | 0.84 | 0.85 |  |  | 0.83 | 0.85 |  | 0.85
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.1 | 36.7 |  | 37.3 | 36.4 | 36.8 |  |  | 36.5 | 37.1 |  | 36.8
| SATURATED TEMEPRATURE | CELCIUS | C | 36.4 | 37 |  | 38.2 | 37.2 | 37.6 |  |  | 36.9 | 37.5 |  | 36.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.9 | 2.2 | 0 | 4.3 | 3.7 | 2.9 | 0 | 0 | 3.3 | 2.3 | 0 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.3 | 29.2 |  | 29 | 28.2 | 29.2 |  |  | 28 | 28.9 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.5 | 34.8 |  | 33.9 | 33.5 | 34.7 |  |  | 33.6 | 35.2 |  | 34.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.2 | 5.6 | 0 | 4.9 | 5.3 | 5.5 | 0 | 0 | 5.6 | 6.3 | 0 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1295.98 | 1269.52 |  | 1301.02 | 1298.92 | 1293.32 |  |  | 1156.68 | 1089.34 |  | 1265.18
| HEAT CAPACITY | kW | 8226.9 | 7781.8661 | 8209.3672 | 0 | 7361.4296 | 7949.5104 | 8213.9261 | 0 | 0 | 7479.6859 | 7924.7598 | 0 | 8327.3972
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.47 |  | 0.47 | 0.46 | 0.47 |  |  | 0.46 | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.9 | 20.2 |  | 20 | 19.7 | 20.2 |  |  | 19.7 | 20.6 |  | 20.2
| LIQUID LEVEL | mm | mm | 195.9 | 178.1 |  | 128.5 | 204 | 205.5 |  |  | 159 | 162.6 |  | 202.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.56 | 5.22 |  | 5.16 | 5.49 | 5.43 |  |  | 5.71 | 5.34 |  | 5.24
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 16
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK |  |  |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 72.6 | 77.4 | 77.4 | 73.2 | 73.2 |  |  |  | 72.4 | 78 | 77.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.3 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0.2 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 67.4 | 73.3 | 73.2 | 68.8 | 68.8 |  |  |  | 69.1 | 73.5 | 73.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.4 | 65.6 | 68.3 | 61.6 | 63.6 |  |  |  | 71.8 | 70.8 | 72.8
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 60.4 | 46.3 | 48.7 | 37.6 | 39.6 |  |  |  | 48 | 38.6 | 39.3
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  |  |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 117.8 | 115.5 | 117.1 | 116.9 | 116.1 |  |  |  | 116.4 | 117.7 | 118.4
| INPUT | Kw | 1194kW |  | 1167 | 1172 | 1192 | 1179 | 1183 |  |  |  | 1192 | 1197 | 1210
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46334.2 | 47147 | 47137.9 | 44749.5 | 44740.4 |  |  |  | 46364.6 | 48267.7 | 48258.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 | 59.2 | 59.1 | 57.7 | 57.5 |  |  |  | 58.8 | 59.3 | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.49 | 0.59 | 0.59 |  |  |  | 0.48 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.5 | 45.1 | 44.9 | 44.9 | 45 |  |  |  | 44.9 | 45.1 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.22 | 0.24 | 0.23 |  |  |  | 0.22 | 0.23 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 | 3.2 | 3.8 | 4.1 | 4.3 |  |  |  | 4.5 | 4 | 4.2
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 | 2.4 | 2.8 | 3.4 | 3.5 |  |  |  | 3.2 | 3.5 | 3.1
| APPROACH TEMP | CELCIUS | C |  | 0.6 | 2 | 2.1 | 1.2 | 0.8 | 0 | 0 | 0 | 1.4 | 1.1 | 2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 661.5 | 673.76 | 662 | 674.48 | 651.74 |  |  |  | 652.6 | 683.12 | 666.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.3 | 12.3 | 13.5 | 12.9 | 13.1 |  |  |  | 13.4 | 12.5 | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.5 | 4.4 | 4.9 | 4.6 | 4.3 |  |  |  | 4.6 | 4.6 | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8.8 | 7.9 | 8.6 | 8.3 | 8.8 | 0 | 0 | 0 | 8.8 | 7.9 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW |  | 6721.94 | 6146.3095 | 6574.1339 | 6464.4157 | 6622.7621 | 0 | 0 | 0 | 6631.5012 | 6231.6952 | 6465.8661
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.86 | 0.86 | 0.85 | 0.84 |  |  |  | 0.86 | 0.83 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 | 37.1 | 37.1 | 36.7 | 36.6 |  |  |  | 36.7 | 36.8 | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.5 | 38.1 | 37.9 | 37.5 | 37.3 |  |  |  | 37 | 36.9 | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  |  | 2 | 4.6 | 4.2 | 3.6 | 2.9 | 0 | 0 | 0 | 2.2 | 2.8 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.9 | 28.4 | 28.8 | 28.6 | 28.9 |  |  |  | 28.6 | 28.6 | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.5 | 33.5 | 33.7 | 33.9 | 34.4 |  |  |  | 34.8 | 34.1 | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.6 | 5.1 | 4.9 | 5.3 | 5.5 | 0 | 0 | 0 | 6.2 | 5.5 | 5.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1269.4 | 1251.74 | 1301 | 1297.52 | 1296.6 |  |  |  | 1091.7 | 1217.02 | 1272.8
| HEAT CAPACITY | kW | 8226.9 |  | 8208.5912 | 7371.679 | 7361.3164 | 7940.9423 | 8234.7575 | 0 | 0 | 0 | 7815.8661 | 7729.3418 | 8671.5012
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.47 | 0.46 | 0.46 | 0.47 |  |  |  | 0.47 | 0.47 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.2 | 19.8 | 19.9 | 19.9 | 20.1 |  |  |  | 19.8 | 20.1 | 20
| LIQUID LEVEL | mm | mm |  | 133.2 | 126.4 | 136 | 200.2 | 203.5 |  |  |  | 167.5 | 203.3 | 203.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.61 | 5.15 | 5.24 | 5.32 | 5.52 |  |  |  | 5.45 | 5.04 | 5.1
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 17
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK |  |  | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 71.4 | 71.4 | 77.4 | 77.4 |  | 73.2 |  |  | 76.3 | 71.5 |  | 78
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.6 | 0 | 0 |  | 0 |  |  | 0 | 0 |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% | 65.6 | 65.6 | 73.3 | 73.3 |  | 68.8 |  |  | 71.7 | 66.1 |  | 73.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 70.7 | 68.5 | 68.4 | 69.4 |  | 63.7 |  |  | 73 | 72.9 |  | 73.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 76.5 | 67.2 | 53.3 | 49 |  | 37.5 |  |  | 55 | 43.1 |  | 41.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  |  | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 116.9 | 118.8 | 116.4 | 116.1 |  | 116.8 |  |  | 119.1 | 115.7 |  | 117.7
| INPUT | Kw | 1194kW | 1156 | 1161 | 1189 | 1175 |  | 1184 |  |  | 1218 | 1178 |  | 1197
COMPRESSOR | RUNNING TIME | Hr | NA | 46352.3 | 46343.9 | 47170 | 47162 |  | 44764.5 |  |  | 46506 | 46374.4 |  | 48282.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.5 | 59.2 | 59.3 |  | 57.9 |  |  | 58.7 | 58.7 |  | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.53 | 0.49 | 0.49 |  | 0.59 |  |  | 0.48 | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 44.9 | 44.8 | 44.8 |  | 45 |  |  | 44.8 | 45 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.21 | 0.23 | 0.22 | 0.22 |  | 0.23 |  |  | 0.22 | 0.23 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.7 | 5 | 3.7 | 3.5 |  | 4.2 |  |  | 4.5 | 4.6 |  | 4
| SATURATION TEMPERATURE | CELCIUS | C | 4.3 | 4.5 | 2.9 | 2.7 |  | 3.4 |  |  | 3.7 | 3.5 |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0.7 | 0.9 | 1.7 | 2.4 | 0 | 0.8 | 0 | 0 | 0.5 | 1.3 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 750.56 | 731.1 | 673.6 | 652.4 |  | 657.5 |  |  | 663.76 | 648.5 |  | 629.7
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.8 | 13.5 | 12.8 | 13.6 |  | 12.9 |  |  | 12.8 | 13.6 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5 | 5.4 | 4.6 | 5.1 |  | 4.2 |  |  | 4.2 | 4.8 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.8 | 8.1 | 8.2 | 8.5 | 0 | 8.7 | 0 | 0 | 8.6 | 8.8 | 0 | 8.7
| CHILLING CAPACITY | kW | 7032.6kW | 1143.1871 | 6838.2333 | 6378.1986 | 6403.4642 | 0 | 6605.3695 | 0 | 0 | 6591.612 | 6589.8383 | 0 | 6326.0855
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.82 | 0.85 | 0.85 |  | 0.84 |  |  | 0.82 | 0.83 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.9 | 36.3 | 36.7 | 36.9 |  | 36.6 |  |  | 36.3 | 36.7 |  | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C | 36.4 | 36.7 | 37.7 | 37.9 |  | 37.3 |  |  | 36.8 | 37.1 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.3 | 2 | 4.4 | 4.2 | 0 | 2.9 | 0 | 0 | 2.5 | 2.3 | 0 | 2.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.6 | 28.8 | 28.3 | 28.7 |  | 28.9 |  |  | 28.2 | 28.7 |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.1 | 34.7 | 33.3 | 33.7 |  | 34.4 |  |  | 34.3 | 34.8 |  | 34.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | -5.5 | 5.9 | 5 | 5 | 0 | 5.5 | 0 | 0 | 6.1 | 6.1 | 0 | 5.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1283.94 | 1266.4 | 1303.12 | 1300 |  | 1296.5 |  |  | 1111.3 | 1087.6 |  | 1264.9
| HEAT CAPACITY | kW | 8226.9 | -8154.3533 | 8627.8984 | 7523.7875 | 7505.7737 | 0 | 8234.1224 | 0 | 0 | 7827.8637 | 7660.9238 | 0 | 8617.679
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.47 | 0.47 | 0.47 |  | 0.46 |  |  | 0.46 | 0.47 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 20.2 | 20.3 | 19.8 | 19.9 |  | 19.7 |  |  | 19.7 | 20.2 |  | 19.9
| LIQUID LEVEL | mm | mm | 221.3 | 174.6 | 120 | 128.4 |  | 201.8 |  |  | 149.7 | 160.1 |  | 189.5
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.56 | 5.15 | 5.26 | 5.34 |  | 5.44 |  |  | 5.63 | 5.63 |  | 5.41
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 18
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.4 | 80.8 | 76.2 | 73.3 | 74.1 | 75.1 | 73.5 |  | 76.1 |  | 79.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.7 | 0 | 0 | 0 | 0 | 0.1 | 0.1 |  | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.6 | 76.8 | 72.1 | 68.5 | 69.6 | 69.3 | 69.4 |  | 71.6 |  | 75.4
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 65.4 | 67.8 | 66.6 | 62 | 62.1 | 63 | 64.3 |  | 71.2 |  | 72.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 75.2 | 50.1 | 48.3 | 38.7 | 39.4 | 30.6 | 30.4 |  | 40.7 |  | 40.1
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 116.9 | 118.5 | 114.5 | 116.6 | 115.4 | 116.7 | 116.3 |  | 118.2 |  | 118.8
| INPUT | Kw | 1194kW |  | 1153 | 1206 | 1165 | 1198 | 1186 | 1190 | 1184 |  | 1208 |  | 1210
COMPRESSOR | RUNNING TIME | Hr | NA |  | 3528 | 47186 | 3535 | 44782.2 | 3225 | 47077 | 3310 |  | 3179 |  | 3394
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 | 59.2 | 59.2 | 57.5 | 57.5 | 57.5 | 57.5 |  | 58.7 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.49 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 46.7 | 45 | 44.9 | 44.9 | 45.1 | 45 | 44.9 |  | 44.8 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.28 | 0.22 | 0.22 | 0.23 | 0.22 | 0.22 | 0.22 |  | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 | 3.5 | 3.4 | 4.7 | 4.3 | 4 | 3.9 |  | 4.1 |  | 3.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.1 | 2.6 | 2.6 | 3.7 | 3.3 | 3.4 | 2.9 |  | 2.5 |  | 3.9
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 2.3 | 2.2 | 0.8 | 0.7 | 0.8 | 1.3 | 0 | 1.7 | 0 | 0.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 719 | 678.5 | 654.7 | 673.03 | 655.73 | 648.4 | 636 |  | 641.7 |  | 648.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.2 | 13.1 | 13 | 13 | 12.8 | 13 | 13.1 |  | 13.2 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 | 4.9 | 4.8 | 4.5 | 4 | 4.2 | 4.2 |  | 4.2 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.2 | 8.2 | 8.2 | 8.5 | 8.8 | 8.8 | 8.9 | 0 | 9 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6808.0831 | 6424.5958 | 6199.2379 | 6605.9527 | 6663.3072 | 6588.8222 | 6536.2587 | 0 | 6668.9376 | 0 | 6590.8545
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.87 | 0.85 | 0.85 | 0.84 | 0.85 | 0.84 |  | 0.83 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 | 37.5 | 36.8 | 36.9 | 36.5 | 37.4 | 37 |  | 36.8 |  | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.6 | 38.4 | 37.7 | 37.6 | 37.2 | 37.9 | 37.5 |  | 37.1 |  | 36.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2 | 4.4 | 4.1 | 2.8 | 2.8 | 3.5 | 3.5 | 0 | 2.2 | 0 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28 | 29.2 | 28.7 | 29.3 | 28.9 | 29 | 28.7 |  | 28.6 |  | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.6 | 34 | 33.6 | 34.8 | 34.4 | 34.4 | 34 |  | 34.9 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 6.6 | 4.8 | 4.9 | 5.5 | 5.5 | 5.4 | 5.3 | 0 | 6.3 | 0 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1260.3 | 1278.8 | 1302.5 | 1301.4 | 1299.3 | 1236.8 | 1262.4 |  | 1084.8 |  | 1264.8
| HEAT CAPACITY | kW | 8226.9 | 0 | 9605.0577 | 7088.037 | 7369.8037 | 8265.2425 | 8251.9053 | 7712.1478 | 7726.0046 | 0 | 7891.7321 | 0 | 8324.8961
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.47 | 0.46 | 0.48 | 0.47 | 0.47 | 0.47 |  | 0.46 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 | 20 | 19.7 | 20.3 | 20 | 20.5 | 20.1 |  | 19.7 |  | 19.9
| LIQUID LEVEL | mm | mm |  | 213.2 | 113.3 | 133.5 | 208.6 | 202.5 | 216.9 | 212.1 |  | 159.7 |  | 205.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.21 | 5.13 | 5.33 | 5.28 | 5.48 | 5.47 | 5.62 |  | 5.47 |  | 5.37
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 19
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.5 | 83.9 | 76.1 |  | 74.2 |  | 73.5 | 74.1 | 76.1 |  | 79.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.9 | 81 | 72.3 |  | 69.3 |  | 69.4 | 68.7 | 71.6 |  | 75.4
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 65.3 | 68.3 | 65.9 |  | 62.3 |  | 64.3 | 73 | 71.2 |  | 72.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 75.3 | 60.5 | 48.5 |  | 40.1 |  | 31.5 | 58.5 | 40.7 |  | 40.1
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 115.9 | 117.8 | 114.3 |  | 115.4 |  | 116.3 | 114.7 | 118.2 |  | 118.8
| INPUT | Kw | 1194kW |  | 1156 | 1200 | 1160 |  | 1186 |  | 1179 | 1172 | 1208 |  | 1210
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46385.3 | 47209.5 | 47207.7 |  | 44799.6 |  | 47100.3 | 46417.6 | 46415.8 |  | 48309.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.4 | 59.1 | 59.2 |  | 57.6 |  | 57.6 | 58.4 | 58.7 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.51 | 0.48 | 0.49 |  | 0.59 |  | 0.52 | 0.48 | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 46.6 | 45 | 44.9 |  | 45 |  | 44.9 | 45 | 44.8 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.28 | 0.21 | 0.22 |  | 0.22 |  | 0.22 | 0.22 | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.4 | 2.9 | 3.4 |  | 4.3 |  | 3.9 | 4.2 | 4.1 |  | 3.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.1 | 1.9 | 2.6 |  | 3.3 |  | 2.9 | 3.6 | 2.5 |  | 3.9
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 2.7 | 2.2 | 0 | 0.7 | 0 | 1.3 | 0.8 | 1.7 | 0 | 0.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 711.3 | 682.5 | 654.7 |  | 655.73 |  | 636 | 680.6 | 641.7 |  | 648.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.9 | 13.2 | 13 |  | 12.8 |  | 13.1 | 13.2 | 13.2 |  | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 | 4.6 | 4.8 |  | 4 |  | 4.2 | 4.4 | 4.2 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 7.9 | 8.6 | 8.2 | 0 | 8.8 | 0 | 8.9 | 8.8 | 9 | 0 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6488.7644 | 6777.7136 | 6199.2379 | 0 | 6663.3072 | 0 | 6536.2587 | 6916.0277 | 6668.9376 | 0 | 6590.8545
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.81 | 0.85 |  | 0.84 |  | 0.84 | 0.79 | 0.8 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 | 35.1 | 36.8 |  | 36.5 |  | 37 | 34.5 | 36.8 |  | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.6 | 36.1 | 37.7 |  | 37.2 |  | 37.5 | 35 | 37.1 |  | 36.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2 | 4.6 | 4.1 | 0 | 2.8 | 0 | 3.5 | 2.5 | 2.2 | 0 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.9 | 26.7 | 28.7 |  | 28.9 |  | 28.7 | 26.6 | 28.6 |  | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.6 | 31.5 | 33.6 |  | 34.4 |  | 34 | 32.5 | 34.9 |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.7 | 4.8 | 4.9 | 0 | 5.5 | 0 | 5.3 | 5.9 | 6.3 | 0 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1260.3 | 1299.5 | 1302.5 |  | 1299.3 |  | 1262.4 | 1177.6 | 1084.8 |  | 1264.8
| HEAT CAPACITY | kW | 8226.9 | 0 | 8295.2771 | 7202.7714 | 7369.8037 | 0 | 8251.9053 | 0 | 7726.0046 | 8022.9099 | 7891.7321 | 0 | 8324.8961
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.43 | 0.46 |  | 0.47 |  | 0.47 | 0.44 | 0.46 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 | 17.9 | 19.7 |  | 20 |  | 20.1 | 18.6 | 19.7 |  | 19.9
| LIQUID LEVEL | mm | mm |  | 213.2 | 113.7 | 133.5 |  | 202.5 |  | 212.1 | 160.4 | 159.7 |  | 205.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.2 | 5.24 | 5.33 |  | 5.48 |  | 5.62 | 5.53 | 5.47 |  | 5.37
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 20
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 70.2 | 70.2 |  | 83.9 |  | 73.1 |  | 72.3 |  | 72.3 | 79.2 | 79.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0 |  | 0 |  | 0 |  | 0.1 |  | 0 | 0.2 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% | 64.8 | 64.8 |  | 80.9 |  | 67.8 |  | 68.1 |  | 67.3 | 74.8 | 74.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 66 | 64.6 |  | 66.1 |  | 62.6 |  | 66.1 |  | 70.6 | 72.3 | 71.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 72.1 | 53.1 |  | 50 |  | 39.2 |  | 30.9 |  | 40.7 | 39.1 | 42.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 116.9 | 117.8 |  | 120.6 |  | 116.6 |  | 118.1 |  | 117.2 | 119.1 | 120.6
| INPUT | Kw | 1194kW | 1146 | 1150 |  | 1218 |  | 1183 |  | 1191 |  | 1185 | 1213 | 1215
COMPRESSOR | RUNNING TIME | Hr | NA | 46395.5 | 46386.9 |  | 47223.6 |  | 44801.1 |  | 47106 |  | 46431.7 | 48320.8 | 48311.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.4 | 58 |  | 59.2 |  | 57.6 |  | 57.6 |  | 58.7 | 59.3 | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 |  | 0.48 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.4 | 44.9 |  | 45.1 |  | 44.9 |  | 45 |  | 44.8 | 45 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.28 |  | 0.21 |  | 0.23 |  | 0.22 |  | 0.22 | 0.22 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.5 | 4.4 |  | 2.9 |  | 4.1 |  | 4.4 |  | 4.4 | 4.2 | 4.1
| SATURATION TEMPERATURE | CELCIUS | C | 4.2 | 4 |  | 2.1 |  | 3.4 |  | 2.9 |  | 3.2 | 3.2 | 3.2
| APPROACH TEMP | CELCIUS | C | 1.1 | 1 | 0 | 2.4 | 0 | 1.3 | 0 | 0.7 |  | 1.2 | 1.7 | 1.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 764.6 | 731.2 |  | 649.12 |  | 637.92 |  | 646.32 |  | 644 | 685.8 | 653.28
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13 | 12.8 |  | 13 |  | 13.6 |  | 12.4 |  | 13 | 13.2 | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5.3 | 5 |  | 4.5 |  | 4.7 |  | 3.6 |  | 4.4 | 4.9 | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.7 | 7.8 | 0 | 8.5 | 0 | 8.9 | 0 | 8.8 | 0 | 8.6 | 8.3 | 8.3
| CHILLING CAPACITY | kW | 7032.6kW | 6798.4065 | 6585.8661 | 0 | 6371.2702 | 0 | 6555.9908 | 0 | 6567.6859 | 0 | 6395.3811 | 6572.9099 | 6261.2286
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.83 | 0.83 |  | 0.87 |  | 0.85 |  | 0.85 |  | 0.84 | 0.83 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.7 | 36.3 |  | 37.1 |  | 36.7 |  | 37.4 |  | 36.9 | 37 | 36.7
| SATURATED TEMEPRATURE | CELCIUS | C | 37.1 | 36.8 |  | 38.2 |  | 37.4 |  | 37.5 |  | 37.2 | 37.1 | 36
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2 | 2.8 | 0 | 4.7 | 0 | 3.7 | 0 | 4.2 | 0 | 3 | 2.3 | 2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.1 | 28.7 |  | 28.3 |  | 28.4 |  | 28.2 |  | 28.4 | 29 | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 35.1 | 34 |  | 33.5 |  | 33.7 |  | 33.3 |  | 34.2 | 34.8 | 34
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 6 | 5.3 | 0 | 5.2 | 0 | 5.3 | 0 | 5.1 | 0 | 5.8 | 5.8 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1208.5 | 1260.42 |  | 1300.32 |  | 1292.2 |  | 1258.88 |  | 1079.82 | 1215.3 | 1265.32
| HEAT CAPACITY | kW | 8226.9 | 8372.9792 | 7713.8868 | 0 | 7807.9261 | 0 | 7908.3834 | 0 | 7413.7275 | 0 | 7232.0508 | 8139.4226 | 7743.8753
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.48 | 0.47 |  | 0.46 |  | 0.47 |  | 0.48 |  | 0.47 | 0.47 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 20.5 | 20.4 |  | 19.5 |  | 19.9 |  | 20.5 |  | 20.1 | 20.2 | 20
| LIQUID LEVEL | mm | mm | 227 | 228.9 |  | 126.9 |  | 200.1 |  | 212.9 |  | 159.2 | 201.6 | 199.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.01 | 5.13 |  | 5.31 |  | 5.67 |  | 5.39 |  | 5.54 | 5.03 | 5.14
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 21
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.2 |  | 74.1 |  | 72.4 |  | 73.3 |  | 73.7 |  | 78.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.2 |  | 0 |  | 0 |  | 0.2 |  | 0 |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.8 |  | 68.4 |  | 66.8 |  | 67.5 |  | 67.9 |  | 75.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.3 |  | 68.7 |  | 63.6 |  | 64.4 |  | 72.3 |  | 73.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 74.7 |  | 47.5 |  | 35.7 |  | 32.1 |  | 45.3 |  | 38.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.6 |  | 115.3 |  | 116.3 |  | 116.6 |  | 117.8 |  | 119.8
| INPUT | Kw | 1194kW |  | 1153 |  | 1172 |  | 1188 |  | 1188 |  | 1195 |  | 1214
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46411 |  | 47233 |  | 44810 |  | 47115 |  | 46446 |  | 48335
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.2 |  | 57.7 |  | 57.7 |  | 58.8 |  | 59.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.5 |  | 0.58 |  | 0.58 |  | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 45 |  | 44.6 |  | 44.6 |  | 44.6 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.24 |  | 0.22 |  | 0.23 |  | 0.22 |  | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 |  | 4 |  | 4.6 |  | 4.3 |  | 4.3 |  | 4.1
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 |  | 2.9 |  | 3.5 |  | 2.9 |  | 2.9 |  | 3
| APPROACH TEMP | CELCIUS | C | 0 | 0.5 | 0 | 1.6 | 0 | 1.1 | 0 | 1 |  | 1.1 | 0 | 1.6
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 674.72 |  | 641.92 |  | 642.56 |  | 643.28 |  | 635.44 |  | 647.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.7 |  | 12.8 |  | 131.3 |  | 12.8 |  | 12.5 |  | 12.9
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.4 |  | 4.5 |  | 4.6 |  | 3.9 |  | 4 |  | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.3 | 0 | 8.3 | 0 | 126.7 | 0 | 8.9 | 0 | 8.5 | 0 | 8.3
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6466.7159 | 0 | 6152.351 | 0 | 94009.6443 | 0 | 6611.0762 | 0 | 6236.9977 | 0 | 6206.7898
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.84 |  | 0.87 |  | 0.85 |  | 0.86 |  | 0.85 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.9 |  | 37.5 |  | 37 |  | 37.7 |  | 37.2 |  | 37.1
| SATURATED TEMEPRATURE | CELCIUS | C |  | 37 |  | 38.2 |  | 37.7 |  | 37.9 |  | 37.4 |  | 37.1
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.8 | 0 | 4.6 | 0 | 3.6 | 0 | 4.2 | 0 | 3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29 |  | 28.8 |  | 28.8 |  | 28.6 |  | 28.8 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.2 |  | 33.6 |  | 34.1 |  | 33.7 |  | 34.4 |  | 34.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.2 | 0 | 4.8 | 0 | 5.3 | 0 | 5.1 | 0 | 5.6 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1257.76 |  | 1301.72 |  | 1299.05 |  | 1258.88 |  | 1080.66 |  | 1261.26
| HEAT CAPACITY | kW | 8226.9 | 0 | 7552.3695 | 0 | 7215.0762 | 0 | 7950.306 | 0 | 7413.7275 | 0 | 6988.1016 | 0 | 7719.0277
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 |  | 0.48 |  | 0.48 |  | 0.48 |  | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.5 |  | 20.5 |  | 20.5 |  | 20 |  | 20.2 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 235.1 |  | 125 |  | 207.1 |  | 216.5 |  | 157.5 |  | 199.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.29 |  | 5.2 |  | 5.5 |  | 5.46 |  | 5.35 |  | 5.05
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 22
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 68.9 | 77.9 | 77.9 | 72.4 | 72.4 |  | 72.4 | 71.2 | 72.2 |  | 77.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.3 | 0 | 0 | 0 | 0 |  | 0.2 | 0 | 0 |  | 72.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 62.8 | 73.9 | 74.2 | 67.2 | 67.2 |  | 69.2 | 66.9 | 67.1 |  | 72.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.4 | 66.5 | 67.5 | 62.5 | 64.2 |  | 64.3 | 70.9 | 71.4 |  | 38.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 73.2 | 46.1 | 46.6 | 39.2 | 36 |  | 29.7 | 45.7 | 45.3 |  | 38.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 117.2 | 116 | 116.6 | 115.6 | 117 |  | 117.4 | 114.9 | 116.7 |  | 118.5
| INPUT | Kw | 1194kW |  | 1157 | 1188 | 1185 | 1192 | 1196 |  | 1192 | 1178 | 1189 |  | 1206
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46424.2 | 47268.1 | 47257.3 | 44830 | 44820.5 |  | 47139.7 | 46471.9 | 46462.4 |  | 48345.6
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 | 59.1 | 59.2 | 57.5 | 57.7 |  | 57.6 | 53.8 | 45.1 |  | 59.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.49 | 0.49 | 0.48 | 0.59 |  | 0.52 | 0.48 | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.5 | 45.2 | 45.1 | 44.9 | 44.8 |  | 44.9 | 44.9 | 45.1 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.24 | 0.22 | 0.22 | 0.23 | 0.23 |  | 0.22 | 0.22 | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.9 | 3.5 | 3.3 | 4.7 | 4.4 |  | 4.1 | 4.3 | 4.3 |  | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.5 | 2.7 | 2.5 | 3.8 | 3.5 |  | 2.9 | 3.3 | 3.2 |  | 3
| APPROACH TEMP | CELCIUS | C | 0 | 0.7 | 2.1 | 2.3 | 0.7 | 1.2 | 0 | 1.1 | 1.3 | 1.2 | 0 | 2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 718 | 678.2 | 642.16 | 674.8 | 646.64 |  | 645.68 | 669.7 | 633.12 |  | 647.36
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.1 | 13.1 | 13.2 | 13 | 13.4 |  | 12.8 | 13 | 13.2 |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5.2 | 4.8 | 4.8 | 4.5 | 4.7 |  | 4 | 4.6 | 4.4 |  | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 7.9 | 8.3 | 8.4 | 8.5 | 8.7 | 0 | 8.8 | 8.4 | 8.8 | 0 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6549.8845 | 6500.0693 | 6228.8037 | 6623.3256 | 6496.2679 | 0 | 6561.1824 | 6495.9353 | 6433.552 | 0 | 6279.2425
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.84 | 0.87 | 0.87 | 0.86 | 0.85 |  | 0.86 | 0.87 | 0.85 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.9 | 37.6 | 37.3 | 37.3 | 37 |  | 37.7 | 37.1 | 37.2 |  | 37.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 37.1 | 38.5 | 30.3 | 38 | 37.7 |  | 38 | 37.4 | 37.6 |  | 37.1
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.8 | 4.2 | -3.3 | 2.8 | 3.6 | 0 | 4.2 | 2.2 | 3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29 | 29.6 | 28.7 | 29.7 | 28.8 |  | 28.6 | 29.4 | 28.8 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.3 | 34.3 | 33.6 | 35.2 | 34.1 |  | 33.8 | 35.2 | 34.6 |  | 34.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 4.7 | 4.9 | 5.5 | 5.3 | 0 | 5.2 | 5.8 | 5.8 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1259.72 | 1309.4 | 1301.3 | 1289.4 | 1295.98 |  | 1258.88 | 1161.7 | 1083.74 |  | 1258.32
| HEAT CAPACITY | kW | 8226.9 | 0 | 7709.6028 | 7106.4434 | 7363.0139 | 8189.03 | 7931.5173 | 0 | 7559.0947 | 7780.4388 | 7258.3048 | 0 | 7701.0346
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 | 0.47 | 0.47 | 0.48 | 0.47 |  | 0.48 | 0.47 | 0.48 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.5 | 20.2 | 20.2 | 20.5 | 20.2 |  | 20.6 | 20.3 | 20.5 |  | 20.4
| LIQUID LEVEL | mm | mm |  | 191.5 | 122.5 | 124.7 | 200.9 | 204 |  | 215.2 | 158.9 | 164.9 |  | 205.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.21 | 5.14 | 5.36 | 5.25 | 5.45 |  | 5.4 | 5.27 | 5.63 |  | 5.21
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 23
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  |  |  | 76.1 | 70.7 | 72.5 | 76.3 | 72.6 |  | 71.1 | 79.1 | 79.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  |  |  | 0 | 0 | 0 | 0.1 | 0.2 |  | 0 | 0.2 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  |  |  | 71.1 | 67 | 67.2 | 71.8 | 39.6 |  | 67.3 | 75.2 | 74.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  |  |  | 69.3 | 61.5 | 63.1 | 63.7 | 64.4 |  | 73.3 | 69.3 | 72.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  |  |  | 50.1 | 39.5 | 38 | 36.8 | 32.1 |  | 50.4 | 39.5 | 41.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  |  |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  |  |  | 117.9 | 113.5 | 117.1 | 118.6 | 117.5 |  | 117.8 | 116.7 | 120.2
| INPUT | Kw | 1194kW |  |  |  | 1198 | 1159 | 1179 | 1208 | 1196 |  | 1200 | 1188 | 1219
COMPRESSOR | RUNNING TIME | Hr | NA |  |  |  | 47279 | 44853.9 | 44844.4 | 47158.7 | 47149 |  | 46486 | 48364.9 | 48355.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  |  |  | 59.1 | 57.8 | 57.4 | 57.3 | 57.6 |  | 58.7 | 59.3 | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  |  |  | 0.5 | 0.58 | 0.59 | 0.52 | 0.52 |  | 0.48 | 0.47 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  |  |  | 45 | 45.3 | 45 | 45 | 44 |  | 44.8 | 45 | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  |  |  | 0.22 | 0.22 | 0.23 | 0.22 | 0.22 |  | 0.28 | 0.22 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  |  |  | 4.2 | 4.1 | 4.1 | 4.2 | 4.1 |  | 4.9 | 3.5 | 4.1
| SATURATION TEMPERATURE | CELCIUS | C |  |  |  | 3.2 | 3.1 | 3.5 | 3.2 | 3 |  | 3.1 | 2.7 | 3.2
| APPROACH TEMP | CELCIUS | C | 0 |  | 0 | 1.9 | 0.8 | 1.3 | 1.3 | 1 | 0 | 1.9 | 1.6 | 1.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  |  |  | 661.28 | 670.1 | 641.68 | 745.6 | 632.8 |  | 652.72 | 671.4 | 627.92
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  |  |  | 13.5 | 12.4 | 13.6 | 12.5 | 13.1 |  | 13.6 | 12.5 | 13.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  |  |  | 5.1 | 3.9 | 4.8 | 4.5 | 4 |  | 5 | 4.3 | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 0 | 0 | 8.4 | 8.5 | 8.8 | 8 | 9.1 | 0 | 8.6 | 8.2 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 0 | 0 | 6414.2633 | 6577.194 | 6520.5358 | 6887.7598 | 6649.515 | 0 | 6481.9769 | 6357.3672 | 6380.7113
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  |  |  | 0.87 | 0.81 | 0.85 | 0.84 | 0.86 |  | 0.85 | 0.8 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  |  |  | 37.7 | 35.5 | 37.1 | 36.6 | 37.6 |  | 37.3 | 35.8 | 37
| SATURATED TEMEPRATURE | CELCIUS | C |  |  |  | 38.6 | 36.3 | 37.7 | 37.2 | 38 |  | 37.6 | 35.9 | 37.1
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 0 | 0 | 4.3 | 2.9 | 2.7 | 3.7 | 3.5 | 0 | 2.2 | 2.2 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  |  |  | 29.4 | 28 | 29.5 | 28 | 29.3 |  | 29.2 | 27.8 | 29.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  |  |  | 34.3 | 33.4 | 35 | 33.5 | 34.5 |  | 35.4 | 33.7 | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 0 | 0 | 4.9 | 5.4 | 5.5 | 5.5 | 5.2 | 0 | 6.2 | 5.9 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  |  |  | 1300.46 | 1295.1 | 1295.14 | 1237 | 1283.66 |  | 1101.8 | 1234.6 | 1278.06
| HEAT CAPACITY | kW | 8226.9 | 0 | 0 | 0 | 7358.261 | 8075.6813 | 8225.485 | 7856.2356 | 7707.8891 | 0 | 7888.1755 | 8411.2471 | 8412.1732
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  |  |  | 0.48 | 0.45 | 0.47 | 0.47 | 0.48 |  | 0.48 | 0.45 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  |  |  | 20.6 | 19.1 | 20.2 | 20 | 20.5 |  | 20.4 | 19.2 | 20.2
| LIQUID LEVEL | mm | mm |  |  |  | 119.9 | 192.9 | 207.3 | 206.8 | 214.8 |  | 156.1 | 198.1 | 193.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.28 |  | 5.28 | 5.44 | 5.54 | 4.93 | 5.41 |  | 5.39 | 5.1 | 5.29
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 24
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  |  |  | OK | OK | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  |  |  | 74.9 | 74.2 | 74.2 |  | 71.7 | 74.4 | 74.3 | 79.1 | 79.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  |  |  | 0 | 0 | 0 |  | 0.2 | 0 | 0 | 0.2 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  |  |  | 70.5 | 68.5 | 68.2 |  | 68.7 | 69.9 | 69.8 | 75.1 | 74.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  |  |  | 67.9 | 61 | 63.1 |  | 64.7 | 68.8 | 72.3 | 69.9 | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  |  |  | 50.9 | 36.8 | 36.8 |  | 30.6 | 48.4 | 47.2 | 38.1 | 40.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  |  |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  |  |  | 117 | 117.5 | 118 |  | 115.8 | 116.6 | 118.6 | 117.8 | 119.6
| INPUT | Kw | 1194kW |  |  |  | 1183 | 1197 | 1191 |  | 1180 | 1192 | 1210 | 1194 | 1216
COMPRESSOR | RUNNING TIME | Hr | NA |  |  |  | 47288.6 | 44877.6 | 44868.4 |  | 47173.2 | 46505.1 | 46496 | 48388.5 | 48379.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  |  |  | 59.2 | 57.9 | 57.5 |  | 57.5 | 58.7 | 58.9 | 59.2 | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  |  |  | 0.5 | 0.59 | 0.59 |  | 0.52 | 0.48 | 0.48 | 0.47 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  |  |  | 45.1 | 45 | 45 |  | 45.1 | 44.9 | 44.9 | 45.2 | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  |  |  | 0.22 | 0.24 | 0.22 |  | 0.22 | 0.22 | 0.23 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  |  |  | 3.9 | 4.3 | 4.1 |  | 4.1 | 4.1 | 4.6 | 3.5 | 4.4
| SATURATION TEMPERATURE | CELCIUS | C |  |  |  | 3.2 | 3.4 | 3.4 |  | 3.6 | 3.5 | 3.5 | 3.3 | 3.3
| APPROACH TEMP | CELCIUS | C | 0 | 0 | 0 | 2.1 | 1 | 1.4 | 0 | 0.7 | 0.5 | 1.3 | 1.1 | 1.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  |  |  | 667.1 | 672.72 | 645.32 |  | 642.6 | 666.24 | 655.8 | 649.6 | 662.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  |  |  | 13.5 | 12.9 | 13.6 |  | 13.3 | 12.3 | 13.6 | 12.5 | 13.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  |  |  | 5.3 | 4.4 | 4.8 |  | 4.3 | 4 | 4.8 | 4.4 | 5.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 0 | 0 | 8.2 | 8.5 | 8.8 | 0 | 9 | 8.3 | 8.8 | 8.1 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 0 | 0 | 6316.6513 | 6602.9099 | 6557.5242 | 0 | 6678.291 | 6385.4411 | 6664.0185 | 6075.9353 | 6506.5242
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  |  |  | 0.87 | 0.86 | 0.85 |  | 0.85 | 0.84 | 0.84 | 0.84 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  |  |  | 37.3 | 36.8 | 37.1 |  | 37.3 | 36.8 | 37.1 | 36.7 | 37
| SATURATED TEMEPRATURE | CELCIUS | C |  |  |  | 38.3 | 37.9 | 37.7 |  | 37.8 | 37.4 | 37.4 | 37 | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 0 | 0 | 4.2 | 3.6 | 2.7 | 0 | 3.6 | 3.1 | 2.2 | 2.7 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  |  |  | 29.2 | 29 | 29.5 |  | 29.2 | 29.8 | 28.9 | 29.1 | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  |  |  | 34.1 | 34.3 | 35 |  | 34.2 | 34.3 | 35.2 | 34.3 | 34.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 0 | 0 | 4.9 | 5.3 | 5.5 | 0 | 5 | 4.5 | 6.3 | 5.2 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  |  |  | 1301 | 1292.76 | 1298.4 |  | 1276.8 | 1150.38 | 1105.9 | 1260 | 1273.3
| HEAT CAPACITY | kW | 8226.9 | 0 | 0 | 0 | 7361.3164 | 7911.8106 | 8246.1894 | 0 | 7371.8245 | 5977.7252 | 8045.2309 | 7565.8199 | 8380.843
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  |  |  | 0.47 | 0.46 | 0.47 |  | 0.47 | 0.46 | 0.47 | 0.46 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  |  |  | 20.4 | 19.8 | 19.9 |  | 20.5 | 19.8 | 20.2 | 19.7 | 20.2
| LIQUID LEVEL | mm | mm |  |  |  | 124.3 | 213.2 | 212.7 |  | 212.9 | 160.2 | 163.3 | 198.1 | 208.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.28 |  | 5.21 | 5.25 | 5.52 |  | 5.6 | 5.23 | 5.39 | 5.26 | 5.26
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 25
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  |  | OK | OK |  | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  |  | 74.4 | 77.7 |  | 74.3 |  | 72.8 | 74.4 | 74.4 | 79.1 | 79.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  |  | 0 | 0 |  | 0 |  | 0.1 | 0 | 0 | 0.2 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  |  | 71.4 | 73.2 |  | 68.5 |  | 67.9 | 69.9 | 69.3 | 75.1 | 74.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  |  | 68.9 | 66.5 |  | 62.7 |  | 65.8 | 73 | 70.4 | 73.8 | 71
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  |  | 71.4 | 47.5 |  | 38.3 |  | 31.5 | 45.7 | 46.1 | 38.7 | 41.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  |  | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  |  | 117.1 | 117 |  | 118.1 |  | 117.4 | 119.2 | 117.1 | 119.6 | 118
| INPUT | Kw | 1194kW |  |  | 1180 | 1186 |  | 1190 |  | 1198 | 1212 | 1197 | 1218 | 1199
COMPRESSOR | RUNNING TIME | Hr | NA |  |  | 47307 | 47297.8 |  | 44891.8 |  | 47184.1 | 46529 | 46519.4 | 48412 | 48402.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  |  | 59.3 | 59.2 |  | 57.8 |  | 57.4 | 58.9 | 58.5 | 59.7 | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  |  | 0.5 | 0.49 |  | 0.59 |  | 0.53 | 0.48 | 0.48 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  |  | 44.8 | 45 |  | 44.8 |  | 44 | 45.6 | 45 | 45.1 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  |  | 0.22 | 0.22 |  | 0.23 |  | 0.23 | 0.23 | 0.22 | 0.22 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  |  | 3.9 | 3.6 |  | 4.2 |  | 4.8 | 4.5 | 4.4 | 4.1 | 3.8
| SATURATION TEMPERATURE | CELCIUS | C |  |  | 3.1 | 2.8 |  | 3.6 |  | 3.7 | 3.7 | 3.6 | 3.2 | 3
| APPROACH TEMP | CELCIUS | C | 0 | 0 | 2 | 2.1 | 0 | 0.8 | 0 | 1.4 | 0.9 | 0.8 | 1.8 | 1.6
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  |  | 673.76 | 658.9 |  | 647.1 |  | 696.9 | 664.76 | 648.1 | 647.52 | 638.1
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  |  | 13.1 | 13.3 |  | 13.3 |  | 13.4 | 13.1 | 13.4 | 13.3 | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  |  | 5.1 | 4.9 |  | 4.4 |  | 5.1 | 4.6 | 4.4 | 5 | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 0 | 8 | 8.4 | 0 | 8.9 | 0 | 8.3 | 8.5 | 9 | 8.3 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 0 | 6224.1109 | 6391.1778 | 0 | 6650.3349 | 0 | 6679.2956 | 6524.7806 | 6735.4503 | 6206.0231 | 6484.157
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  |  | 0.88 | 0.86 |  | 0.85 |  | 0.86 | 0.85 | 0.82 | 0.81 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  |  | 38 | 37.3 |  | 36.8 |  | 37.5 | 37.5 | 37.1 | 37.3 | 36.7
| SATURATED TEMEPRATURE | CELCIUS | C |  |  | 38.8 | 38.3 |  | 37.6 |  | 38 | 37.8 | 37.4 | 37.4 | 36.8
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 0 | 4 | 4.3 | 0 | 2.8 | 0 | 3.6 | 2.2 | 2.3 | 2.3 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  |  | 29.8 | 29.2 |  | 29.2 |  | 29.1 | 29.5 | 29.1 | 29.5 | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  |  | 34.8 | 34 |  | 34.8 |  | 34.4 | 35.6 | 35.1 | 35.1 | 34.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 0 | 5 | 4.8 | 0 | 5.6 | 0 | 5.3 | 6.1 | 6 | 5.6 | 5.6
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  |  | 1299.06 | 1298 |  | 1308.7 |  | 1277.2 | 1116.64 | 1103.6 | 1292.76 | 1280.2
| HEAT CAPACITY | kW | 8226.9 | 0 | 0 | 7500.3464 | 7194.4573 | 0 | 8462.7252 | 0 | 7816.582 | 7865.4781 | 7646.1894 | 8359.649 | 8278.4296
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  |  | 0.48 | 0.47 |  | 0.47 |  | 0.49 | 0.48 | 0.47 | 0.47 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  |  | 20.7 | 20.1 |  | 20.1 |  | 20.9 | 20.4 | 20 | 20.3 | 19.9
| LIQUID LEVEL | mm | mm |  |  | 128.4 | 127.4 |  | 201.3 |  | 209.6 | 160.4 | 164.4 | 202.7 | 201
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  |  | 4.92 | 5.33 |  | 5.52 |  | 5.18 | 5.19 | 5.52 | 5.07 | 5.44
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 26
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  |  | 80.7 | 80.7 | 70.7 | 72.8 | 75.8 | 73 |  | 74.4 |  | 79.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  |  | 0 | 0 | 0 | 0 | 0.1 | 0.1 |  | 0 |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  |  | 76.4 | 76.3 | 67.6 | 67.6 | 70.2 | 70.5 |  | 69.8 |  | 75.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  |  | 70.8 | 68.7 | 63.3 | 63.8 | 64.8 | 64.9 |  | 73 |  | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  |  | 48.6 | 51.3 | 35.9 | 40 | 32.3 | 32.3 |  | 52.3 |  | 39.3
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  |  | 120.5 | 119.4 | 115.9 | 116.5 | 116.3 | 116.1 |  | 118 |  | 118.4
| INPUT | Kw | 1194kW |  |  | 1219 | 1202 | 1183 | 1178 | 1195 | 1187 |  | 1201 |  | 1202
COMPRESSOR | RUNNING TIME | Hr | NA |  |  | 47331 | 47446.2 | 44911.6 | 449903.8 | 47203.1 | 47195.3 |  | 46544.8 |  | 48428.2
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  |  | 59.2 | 59.5 | 58 | 57.5 | 57.2 | 57.4 |  | 58.8 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  |  | 0.49 | 0.49 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  |  | 45.1 | 44.8 | 44.9 | 45 | 45 | 45 |  | 44.9 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  |  | 0.22 | 0.22 | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.23 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  |  | 3.7 | 3.4 | 4.5 | 4.4 | 4 | 4.1 |  | 4.4 |  | 4
| SATURATION TEMPERATURE | CELCIUS | C |  |  | 2.9 | 2.6 | 3.5 | 3.7 | 2.9 | 2.9 |  | 3.1 |  | 3.2
| APPROACH TEMP | CELCIUS | C | 0 | 0 | 2.3 | 2.5 | 0.8 | 0.6 | 1.3 | 1.4 | 0 | 1.6 | 0 | 1.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  |  | 629.9 | 660 | 632.1 | 643.96 | 646.2 | 632.8 |  | 651.2 |  | 636.2
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  |  | 14.2 | 13.5 | 13.2 | 13.3 | 13.1 | 13.3 |  | 13.6 |  | 13.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  |  | 5.2 | 5.1 | 4.3 | 4.3 | 4.2 | 4.3 |  | 4.7 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 0 | 9 | 8.4 | 8.9 | 9 | 8.9 | 9 | 0 | 8.9 | 0 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 0 | 6546.3048 | 6401.8476 | 6496.1778 | 6692.4249 | 6641.0855 | 6576.4434 | 0 | 6692.4711 | 0 | 6538.3141
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  |  | 0.87 | 0.86 | 0.84 | 0.84 | 0.81 | 0.81 |  | 0.86 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  |  | 37.2 | 37.1 | 36.5 | 36.6 | 37 | 37.1 |  | 36.6 |  | 36.4
| SATURATED TEMEPRATURE | CELCIUS | C |  |  | 38.4 | 38.1 | 37.2 | 37.3 | 37.4 | 37.5 |  | 37 |  | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 0 | 4.6 | 4.2 | 2.7 | 2.8 | 3.5 | 3.6 | 0 | 2.2 | 0 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  |  | 29 | 28.8 | 28.8 | 29 | 28.6 | 28.9 |  | 28.6 |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  |  | 33.8 | 33.9 | 34.5 | 34.5 | 33.9 | 33.9 |  | 34.8 |  | 34.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 0 | 4.8 | 5.1 | 5.7 | 5.5 | 5.3 | 5 | 0 | 6.2 | 0 | 5.6
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  |  | 1233.7 | 1301.3 | 1261.2 | 1296.6 | 1255.7 | 1294.1 |  | 1118.1 |  | 1297.9
| HEAT CAPACITY | kW | 8226.9 | 0 | 0 | 6838.06 | 7663.545 | 8301.2009 | 8234.7575 | 7685 | 7471.709 | 0 | 8004.873 | 0 | 8392.8868
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  |  | 0.47 | 0.46 | 0.46 | 47 | 0.47 | 0.47 |  | 0.47 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  |  | 20.1 | 19.9 | 19.5 | 20.1 | 20.1 | 20.1 |  | 20 |  | 19.8
| LIQUID LEVEL | mm | mm |  |  | 126.9 | 124.1 | 211.4 | 200.2 | 203.6 | 210.6 |  | 161.3 |  | 203.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  |  | 5.55 | 5.2 | 5.57 | 5.62 | 5.57 | 5.62 |  | 5.5 |  | 5.53
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 27
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 72.6 | 72.5 |  | 80.8 |  | 75.5 |  | 73 | 76.1 | 74.4 | 77.7 | 79.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.1 | 0.1 |  | 0 |  | 0 |  | 0.1 | 0 | 0 | 0.3 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% | 67.5 | 67.3 |  | 77.6 |  | 70.2 |  | 70.5 | 71.5 | 69.8 | 73.8 | 75.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 65 | 66.1 |  | 52.4 |  | 63.9 |  | 64.9 | 69.3 | 73 | 70.9 | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 64.2 | 62.2 |  | 67.4 |  | 37.5 |  | 32.3 | 48.9 | 52.3 | 40.9 | 39.3
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 119.5 | 117 |  | 119.4 |  | 116.5 |  | 116.1 | 119.7 | 118 | 119.2 | 118.4
| INPUT | Kw | 1194kW | 1172 | 1153 |  | 1202 |  | 1178 |  | 1187 | 1223 | 1201 | 1215 | 1202
COMPRESSOR | RUNNING TIME | Hr | NA | 46449.2 | 46445.7 |  | 47354.7 |  | 44935.3 |  | 47226.8 | 46565.7 | 46562.1 | 48449 | 48445.4
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58 |  | 59.4 |  | 57.5 |  | 57.4 | 58.7 | 58.8 | 59.4 | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 |  | 0.49 |  | 0.59 |  | 0.52 | 0.48 | 0.48 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 45.2 |  | 44.8 |  | 45 |  | 45 | 45.1 | 44.9 | 44.9 | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 | 0.22 | 0.23 | 0.23 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.4 | 4.1 |  | 3.4 |  | 4.4 |  | 4.1 | 4.3 | 4.4 | 4.3 | 4
| SATURATION TEMPERATURE | CELCIUS | C | 4 | 3.7 |  | 2.6 |  | 3.7 |  | 2.9 | 3.3 | 3.1 | 3.2 | 3.2
| APPROACH TEMP | CELCIUS | C | 0.7 | 0.7 | 0 | 2.2 | 0 | 0.6 | 0 | 1.4 | 1.2 | 1.6 | 1.9 | 1.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 678.1 | 658 |  | 660 |  | 643.96 |  | 632.8 | 674.1 | 651.2 | 681.5 | 636.2
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.2 | 13.1 |  | 13.3 |  | 13.3 |  | 13.3 | 13.3 | 13.6 | 13.3 | 13.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.7 | 4.4 |  | 4.8 |  | 4.3 |  | 4.3 | 4.5 | 4.7 | 5.1 | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.5 | 8.7 | 0 | 8.5 | 0 | 9 | 0 | 9 | 8.8 | 8.9 | 8.2 | 8.9
| CHILLING CAPACITY | kW | 7032.6kW | 6655.7159 | 6610.3926 | 0 | 6478.06 | 0 | 6692.4249 | 0 | 6576.4434 | 6849.9769 | 6692.4711 | 6453.0023 | 6538.3141
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.85 | 0.83 |  | 0.86 |  | 0.84 |  | 0.81 | 0.86 | 0.86 | 0.83 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 37.3 | 36.2 |  | 37.1 |  | 36.6 |  | 37.1 | 37.6 | 36.6 | 37.4 | 36.4
| SATURATED TEMEPRATURE | CELCIUS | C | 37.6 | 36.8 |  | 38.1 |  | 37.3 |  | 37.5 | 37.9 | 37 | 37.5 | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.3 | 2.6 | 0 | 4.4 | 0 | 2.8 | 0 | 3.6 | 2.3 | 2.2 | 2.3 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.9 | 28.9 |  | 28.7 |  | 29 |  | 28.9 | 29.7 | 28.6 | 29.6 | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 35.3 | 34.2 |  | 33.7 |  | 34.5 |  | 33.9 | 35.6 | 34.8 | 35.2 | 34.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.4 | 5.3 | 0 | 5 | 0 | 5.5 | 0 | 5 | 5.9 | 6.2 | 5.6 | 5.6
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1300.5 | 1294 |  | 1301.3 |  | 1296.6 |  | 1294.1 | 1140.6 | 1118.1 | 1295.3 | 1297.9
| HEAT CAPACITY | kW | 8226.9 | 8109.3533 | 7919.3995 | 0 | 7513.2794 | 0 | 8234.7575 | 0 | 7471.709 | 7770.8314 | 8004.873 | 8376.0739 | 8392.8868
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.48 | 0.46 |  | 0.46 |  | 47 |  | 0.47 | 0.48 | 0.47 | 0.48 | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 20.5 | 19.5 |  | 19.6 |  | 20.1 |  | 20.1 | 20.5 | 20 | 20.5 | 19.8
| LIQUID LEVEL | mm | mm | 181.6 | 138.8 |  | 114.7 |  | 200.2 |  | 210.6 | 159.6 | 161.3 | 201.6 | 203.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.38 | 5.65 |  | 5.2 |  | 5.62 |  | 5.45 | 5.25 | 5.42 | 5.02 | 5.53
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 28
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 72.6 | 76.1 | 83.9 | 70.5 | 73.1 | 74.8 | 72.3 |  | 72.3 |  | 79.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 | 0 | 0 | 0 | 0 | 0.1 | 0.1 |  | 0 |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 67.5 | 71.2 | 80.9 | 67.5 | 67.8 | 69.2 | 68.1 |  | 67.3 |  | 74.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.5 | 68.4 | 66.1 | 36.3 | 62.6 | 64.1 | 66.1 |  | 70.6 |  | 71.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 72.6 | 51.7 | 50 | 39.4 | 39.2 | 33.4 | 30.9 |  | 40.7 |  | 42.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 118.5 | 116.6 | 120.6 | 114.7 | 116.6 | 116.3 | 118.1 |  | 117.2 |  | 120.6
| INPUT | Kw | 1194kW |  | 1163 | 1188 | 1218 | 1178 | 1183 | 1189 | 1191 |  | 1185 |  | 1215
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46461.4 | 47364.6 | 47355.7 | 44945.6 | 44936.7 | 47236.5 | 47227.6 |  | 46573.8 |  | 48459.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 | 59.2 | 59.2 | 57.9 | 57.6 | 57.5 | 57.6 |  | 58.7 |  | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.5 | 0.49 | 0.59 | 0.59 | 0.52 | 0.52 |  | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 | 45 | 45.1 | 45.1 | 44.9 | 45 | 45 |  | 44.8 |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.22 | 0.21 | 0.22 | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.1 | 4 | 2.9 | 4.4 | 4.1 | 2.8 | 4.4 |  | 4.4 |  | 4.1
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.7 | 3.1 | 2.1 | 3.4 | 3.4 | 3.9 | 2.9 |  | 3.2 |  | 3.2
| APPROACH TEMP | CELCIUS | C | 0 | 0.9 | 2.1 | 2.4 | 0.7 | 1.3 | 0.1 | 0.7 |  | 1.2 | 0 | 1.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 653.5 | 677.3 | 656.5 | 642.5 | 632.3 | 655.4 | 641.3 |  | 635.9 |  | 652.5
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.3 | 13.4 | 13 | 12.9 | 13.6 | 12.7 | 12.4 |  | 13 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.6 | 5.2 | 4.5 | 4.1 | 4.7 | 4 | 3.6 |  | 4.4 |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.7 | 8.2 | 8.5 | 8.8 | 8.9 | 8.7 | 8.8 | 0 | 8.6 | 0 | 8.3
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6565.1848 | 6413.2333 | 6443.7067 | 6528.8684 | 6498.2333 | 6584.2725 | 6516.6744 | 0 | 6314.9423 | 0 | 6253.7529
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.86 | 0.87 | 0.84 | 0.85 | 0.85 | 0.85 |  | 0.84 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 | 37.4 | 37.1 | 36.8 | 36.7 | 37.4 | 37.4 |  | 36.9 |  | 36.7
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.8 | 38.3 | 38.2 | 37.5 | 37.4 | 37.8 | 37.5 |  | 37.2 |  | 36
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.5 | 4.3 | 4.7 | 2.8 | 3.7 | 3.5 | 4.2 | 0 | 3 | 0 | 2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.7 | 29.1 | 28.3 | 29.3 | 28.4 | 29.2 | 28.2 |  | 28.4 |  | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.3 | 34 | 33.5 | 34.7 | 33.7 | 34.3 | 33.3 |  | 34.2 |  | 34
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.6 | 4.9 | 5.2 | 5.4 | 5.3 | 5.1 | 5.1 | 0 | 5.8 | 0 | 5.3
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1295.2 | 1301.2 | 1302.7 | 1297.8 | 1295.8 | 1280.8 | 1288.2 |  | 1107.5 |  | 1291.9
| HEAT CAPACITY | kW | 8226.9 | 0 | 8375.4273 | 7362.448 | 7822.2171 | 8092.5173 | 7930.4157 | 7542.8176 | 7586.3972 | 0 | 7417.4365 | 0 | 7906.5473
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.47 | 0.46 | 0.46 | 0.47 | 0.47 | 0.48 |  | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 | 20.3 | 19.5 | 19.7 | 19.9 | 20.3 | 20.5 |  | 20.1 |  | 20
| LIQUID LEVEL | mm | mm |  | 199.3 | 124.8 | 126.9 | 191.9 | 200.1 | 204.4 | 212.9 |  | 159.2 |  | 199.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.6 | 5.19 | 5.31 | 5.54 | 5.67 | 5.43 | 5.39 |  | 5.54 |  | 5.14
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 29
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 72.5 |  | 75.5 |  | 73.6 |  | 74.7 |  | 74.4 |  | 75.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 |  | 0 |  | 0.1 |  | 0 |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.9 |  | 70.4 |  | 70.4 |  | 69.2 |  | 69.5 |  | 71.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.3 |  | 69.4 |  | 63.2 |  | 65.4 |  | 71.7 |  | 74.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 47.2 |  | 47.5 |  | 38 |  | 33.9 |  | 47.2 |  | 42.1
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 120.1 |  | 115.9 |  | 196.9 |  | 117.4 |  | 118.1 |  | 117.5
| INPUT | Kw | 1194kW |  | 1181 |  | 1177 |  | 1199 |  | 1194 |  | 1205 |  | 1194
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46470 |  | 47375 |  | 44960 |  | 47251 |  | 46583 |  | 48468
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.5 |  | 58.9 |  | 57.7 |  | 57.5 |  | 58.9 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 |  | 0.59 |  | 0.59 |  | 0.49 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 |  | 45.2 |  | 45 |  | 44.6 |  | 44.8 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.24 |  | 0.22 |  | 0.23 |  | 0.22 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.9 |  | 3.7 |  | 4 |  | 4 |  | 4.4 |  | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.3 |  | 2.8 |  | 3.4 |  | 2.9 |  | 3.2 |  | 3.4
| APPROACH TEMP | CELCIUS | C | 0 | 0.7 | 0 | 1.9 | 0 | 1.1 | 0 | 1.1 |  | 1.1 | 0 | 1.6
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 724.8 |  | 647.44 |  | 646.88 |  | 649.36 |  | 635.92 |  | 650.64
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.9 |  | 13.2 |  | 13.3 |  | 13 |  | 13.1 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 |  | 4.7 |  | 4.5 |  | 4 |  | 4.3 |  | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 7.9 | 0 | 8.5 | 0 | 8.8 | 0 | 9 | 0 | 8.8 | 0 | 8.3
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6611.9169 | 0 | 6354.7806 | 0 | 6573.3764 | 0 | 6748.545 | 0 | 6462.0046 | 0 | 6235.9261
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.84 |  | 0.86 |  | 0.84 |  | 0.85 |  | 0.84 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.7 |  | 37.1 |  | 36.7 |  | 37.2 |  | 36.9 |  | 36.6
| SATURATED TEMEPRATURE | CELCIUS | C |  | 37.2 |  | 38 |  | 37.4 |  | 37.6 |  | 37.2 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 3.4 | 0 | 4.7 | 0 | 3.7 | 0 | 4.3 | 0 | 3.2 | 0 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.5 |  | 28.3 |  | 28.3 |  | 28.1 |  | 28.3 |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.8 |  | 33.3 |  | 33.7 |  | 33.3 |  | 34 |  | 33.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.3 | 0 | 5 | 0 | 5.4 | 0 | 5.2 | 0 | 5.7 | 0 | 5.1
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1298.64 |  | 1302.14 |  | 1293.18 |  | 1288.56 |  | 1107.82 |  | 1295.98
| HEAT CAPACITY | kW | 8226.9 | 0 | 7947.7968 | 0 | 7518.1293 | 0 | 8063.709 | 0 | 7737.3118 | 0 | 7291.6559 | 0 | 7632.2148
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 |  | 0.47 |  | 0.46 |  | 0.48 |  | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.5 |  | 20.3 |  | 19.5 |  | 20.4 |  | 20.1 |  | 196.5
| LIQUID LEVEL | mm | mm |  | 166.8 |  | 129.1 |  | 196.9 |  | 212.5 |  | 169.3 |  | 5.27
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 4.96 |  | 5.44 |  | 5.59 |  | 5.5 |  | 5.5
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 30
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 68.5 | 80.6 | 78 | 63.4 | 72 | 75.1 | 73 |  | 74.3 |  | 73.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.1 | 0.2 | 0 | 0 | 0 | 0.1 | 0 |  | 0 |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 61.7 | 77.7 | 73.2 | 57.5 | 66.2 | 69.3 | 67.8 |  | 68.6 |  | 68.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 64.7 | 61.9 | 66.3 | 59.6 | 62.5 | 63 | 64.4 |  | 70.5 |  | 71.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 48.4 | 51.4 | 50.3 | 35 | 35.4 | 30.6 | 28.7 |  | 47.2 |  | 36.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 113.4 | 117.1 | 116.4 | 110.3 | 115.8 | 117.7 | 116.9 |  | 116.4 |  | 114.5
| INPUT | Kw | 1194kW |  | 1109 | 1188 | 1183 | 1128 | 1167 | 1200 | 1184 |  | 1183 |  | 1164
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46491.1 | 47395.8 | 47385.9 | 44980.3 | 44970.3 | 47271.1 | 47261.1 |  | 46602.1 |  | 48493.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 45.7 | 58.7 | 58.9 | 57.9 | 57.7 | 57.5 | 57.5 |  | 44.9 |  | 59.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.48 | 0.49 | 0.59 | 0.59 | 0.52 | 0.59 |  | 0.43 |  | 0.47
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.2 | 45.1 | 45.1 | 45.1 | 45.1 | 45 | 45 |  | 44.9 |  | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.28 | 0.21 | 0.22 | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.22 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 | 2.7 | 3.4 | 4.2 | 4 | 4.2 | 4.2 |  | 3.9 |  | 4
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.7 | 1.8 | 2.5 | 3.3 | 3.4 | 3.1 | 2.9 |  | 3.2 |  | 3.2
| APPROACH TEMP | CELCIUS | C | 0 | 0.6 | 2.3 | 1.8 | 0.7 | 1.2 | 1.4 | 1.6 |  | 0.7 | 0 | 1.5
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 669.2 | 674.3 | 650 | 658.9 | 646.8 | 748.6 | 706.24 |  | 639.12 |  | 649.04
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.4 | 12.3 | 12.5 | 12.2 | 13.2 | 12.3 | 12.8 |  | 12.4 |  | 12.8
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.3 | 4.1 | 4.3 | 4 | 4.6 | 4.5 | 4.5 |  | 3.9 |  | 4.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.1 | 8.2 | 8.2 | 8.2 | 8.6 | 7.8 | 8.3 | 0 | 8.5 | 0 | 8.1
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6259.261 | 6384.8268 | 6154.7344 | 6239.0069 | 6423.1871 | 6742.5866 | 6768.8129 | 0 | 6273.1178 | 0 | 6070.6975
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.84 | 0.87 | 0.81 | 0.85 | 0.85 | 0.86 |  | 0.84 |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.4 | 36.4 | 37.3 | 35.6 | 36.9 | 36.6 | 37.3 |  | 36.9 |  | 36.6
| SATURATED TEMEPRATURE | CELCIUS | C |  | 37 | 37.2 | 38.2 | 36.3 | 37.6 | 37 | 38 |  | 37.3 |  | 36.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 3.2 | 4.3 | 4.7 | 2.9 | 3.6 | 3.5 | 4.4 | 0 | 3 | 0 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.8 | 28 | 28.7 | 28.1 | 28.7 | 28.1 | 28.5 |  | 28.7 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.8 | 32.9 | 33.5 | 33.4 | 34 | 33.5 | 33.6 |  | 34.3 |  | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5 | 4.9 | 4.8 | 5.3 | 5.3 | 5.4 | 5.1 | 0 | 5.6 | 0 | 4.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1298.5 | 1299.6 | 1299.2 | 1298.5 | 1284.22 | 1271 | 1291.92 |  | 1108.94 |  | 1288.56
| HEAT CAPACITY | kW | 8226.9 | 0 | 7497.1132 | 7353.3949 | 7201.1085 | 7946.94 | 7859.545 | 7925.4042 | 7608.3048 | 0 | 7170.9746 | 0 | 7290.9284
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.45 | 0.47 | 0.46 | 0.47 | 0.47 | 0.48 |  | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.3 | 18.8 | 20 | 19.4 | 20.2 | 19.9 | 20.5 |  | 19.9 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 216.8 | 126 | 125.2 | 206.8 | 206 | 212.1 | 229.8 |  | 157.5 |  | 196
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.73 | 5.21 | 5.37 | 5.42 | 5.51 | 4.84 | 5.21 |  | 5.46 |  | 5.17
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 31
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 73.8 | 69.4 |  | 78.7 |  | 74.1 |  | 74.7 | 72.7 | 72.8 | 82.4 | 76.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0 |  | 0 |  | 0 |  | 0.1 | 0 | 0 | 0.3 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% | 68.4 | 63.4 |  | 74.4 |  | 38.4 |  | 70.9 | 69.1 | 68 | 78.2 | 71.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 62.8 | 67.4 |  | 68.2 |  | 63 |  | 64.2 | 69.7 | 72.6 | 70.2 | 72.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 68.4 | 58.1 |  | 46.7 |  | 38.1 |  | 30.2 | 44.8 | 49.8 | 42.4 | 39.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 115.5 | 115.8 |  | 117 |  | 117.8 |  | 118.4 | 112.7 | 117.8 | 117.8 | 117.5
| INPUT | Kw | 1194kW | 1132 | 1139 |  | 1192 |  | 1192 |  | 1204 | 1159 | 1195 | 1197 | 1201
COMPRESSOR | RUNNING TIME | Hr | NA | 46510 | 46501.3 |  | 47410.4 |  | 44986.5 |  | 47285.6 | 46622 | 46613.8 | 48512 | 48503.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 57.8 | 58.1 |  | 59.2 |  | 57.6 |  | 57.6 | 45.1 | 58.9 | 59 | 59.5
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 |  | 0.59 |  | 0.52 | 0.57 | 0.48 | 0.47 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 44.8 |  | 45 |  | 44.9 |  | 44.6 | 45.1 | 44.9 | 45 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 |  | 0.23 |  | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.7 | 4.4 |  | 3.4 |  | 4.2 |  | 4 | 3.9 | 4.4 | 3.4 | 4.3
| SATURATION TEMPERATURE | CELCIUS | C | 3.5 | 4 |  | 2.6 |  | 3.5 |  | 2.8 | 2.8 | 3.4 | 2.7 | 3.6
| APPROACH TEMP | CELCIUS | C | 0.8 | 0.8 | 0 | 2.3 | 0 | 0.7 | 0 | 1.5 | 1.1 | 1.2 | 1.7 | 1.4
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 695.6 | 670.7 |  | 648 |  | 638.5 |  | 633.1 | 662.8 | 641.8 | 675.52 | 648.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.3 | 13.3 |  | 13.4 |  | 13.2 |  | 13.1 | 12.4 | 13.4 | 12.6 | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 4.8 |  | 4.9 |  | 4.2 |  | 4.3 | 3.9 | 4.6 | 4.4 | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8 | 8.5 | 0 | 8.5 | 0 | 9 | 0 | 8.8 | 8.5 | 8.8 | 8.2 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW | 6425.8661 | 6583.0831 | 0 | 6360.2771 | 0 | 6635.6813 | 0 | 6433.3487 | 6505.5427 | 6521.7552 | 6396.3788 | 6291.2702
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.84 |  | 0.87 |  | 0.85 |  | 0.86 | 0.81 | 0.83 | 0.8 | 0.48
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.9 | 36.9 |  | 37.5 |  | 37.2 |  | 37.7 | 35 | 37.2 | 34.9 | 37
| SATURATED TEMEPRATURE | CELCIUS | C | 35.9 | 37.8 |  | 38.4 |  | 37.8 |  | 38 | 36 | 37.5 | 35.8 | 37
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 3.4 | 3 | 0 | 4.2 | 0 | 2.8 | 0 | 3.4 | 3.1 | 2.2 | 2.9 | 2.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.4 | 29.5 |  | 29.4 |  | 29.5 |  | 29.4 | 27.3 | 29.2 | 27.5 | 29.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 32.5 | 34.8 |  | 34.2 |  | 35 |  | 34.6 | 32.9 | 35.3 | 32.9 | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.1 | 5.3 | 0 | 4.8 | 0 | 5.5 | 0 | 5.2 | 5.6 | 6.1 | 5.4 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1291.36 | 1306.4 |  | 1303.6 |  | 1301.2 |  | 1287.9 | 1134.98 | 1108.6 | 1294.44 | 1290
| HEAT CAPACITY | kW | 8226.9 | 7605.0069 | 7995.2887 | 0 | 7225.4965 | 0 | 8263.9723 | 0 | 7733.3487 | 7339.3626 | 7808.8453 | 8071.5658 | 8490.7621
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.48 |  | 0.47 |  | 0.47 |  | 0.48 | 0.44 | 0.47 | 0.44 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 18.8 | 20.5 |  | 20.1 |  | 20.3 |  | 20.4 | 18.5 | 20.3 | 18.6 | 20.3
| LIQUID LEVEL | mm | mm | 200.3 | 202.1 |  | 123.9 |  | 202.4 |  | 213.6 | 160.7 | 159.8 | 194.6 | 202.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.69 | 5.62 |  | 5.4 |  | 5.57 |  | 5.42 | 5.5 | 5.44 | 5.28 | 5.23
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO