## 5
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK
OPENING OF VANE |  | % | 0~100% |  | 70.5 | 77.7 | 81.8 | 71.2 | 74.4 | 73.5 | 73.5 |  |  |  | 78.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 |  |  |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.3 | 75.4 | 77.6 | 67.6 | 68.8 | 67.9 | 68.1 |  |  |  | 73.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 64.4 | 65.9 | 65.6 | 62.6 | 62.6 | 65.3 | 64.9 |  |  |  | 70.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 55.8 | 46.9 | 50.4 | 37.1 | 39.2 | 32.8 | 35.2 |  |  |  | 42.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 116.5 | 117.4 | 119.4 | 115.2 | 117.7 | 118.8 | 118.6 |  |  |  | 120
| INPUT | Kw | 1194kW |  | 1139 | 1206 | 1212 | 1191 | 1209 | 1215 | 1212 |  |  |  | 1221
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45688.6 | 46437 | 46429.2 | 44240 | 44231.8 | 46453 | 46445 |  |  |  | 47572.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 57.9 | 59.2 | 59.2 | 58.2 | 58 | 57.5 | 57.5 |  |  |  | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 5.2 | 4.49 | 0.49 | 0.59 | 0.59 | 0.54 | 0.54 |  |  |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.2 | 45 | 45 | 45.1 | 44.7 | 44.9 | 44.7 |  |  |  | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.22 | 0.21 | 0.23 | 0.23 | 0.23 | 0.23 |  |  |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.2 | 3.9 | 3.3 | 4.8 | 4.7 | 4.8 | 4.7 |  |  |  | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 | 2.8 | 2.5 | 3.9 | 3.7 | 3.7 | 3.6 |  |  |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 0.5 | 1.1 | 1.4 | -0.3 | -0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 696.3 | 712 | 668.1 | 702 | 661.2 | 748 | 701.4 |  |  |  | 687
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.3 | 12.7 | 13.3 | 12.7 | 13.2 | 12.8 | 13.2 |  |  |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 | 5 | 4.7 | 4.5 | 4.4 | 5.1 | 5 |  |  |  | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.6 | 7.7 | 8.6 | 8.2 | 8.8 | 7.7 | 8.2 | 0 | 0 | 0 | 8.2
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6914.7575 | 6330.7159 | 6634.7113 | 6647.1132 | 6718.8915 | 6650.8083 | 6641.4319 | 0 | 0 | 0 | 6505.0808
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.87 | 0.87 | 0.85 | 0.85 | 0.87 | 0.86 |  |  |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.6 | 37.9 | 37.5 | 37.1 | 36.9 | 38.2 | 38 |  |  |  | 37.1
| SATURATED TEMEPRATURE | CELCIUS | C |  | 37 | 38.6 | 38.4 | 37.8 | 37.5 | 38.4 | 38.3 |  |  |  | 37.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2 | 4.1 | 4.3 | 2.7 | 2.6 | 3.3 | 3.4 | 0 | 0 | 0 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.4 | 29.4 | 29.2 | 29.6 | 29.3 | 29.5 | 29.2 |  |  |  | 29.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 35 | 34.5 | 34.1 | 35.1 | 34.9 | 35.1 | 34.9 |  |  |  | 35
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.6 | 5.1 | 4.9 | 5.5 | 5.6 | 5.6 | 5.7 | 0 | 0 | 0 | 5.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1225.3 | 1225.3 | 1286 | 1264.7 | 1297 | 1294 | 1220 | 1198 |  |  |  | 1215
| HEAT CAPACITY | kW | 8226.9 | 0 | 7923.418 | 7573.4411 | 7155.9238 | 8237.2979 | 8367.6674 | 7889.1455 | 7885.2194 | 0 | 0 | 0 | 8277.7136
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.47 | 0.47 | 0.47 | 0.46 | 0.49 | 0.48 |  |  |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.3 | 20.3 | 19.8 | 20.1 | 19.8 | 21.2 | 21 |  |  |  | 20.4
| LIQUID LEVEL | mm | mm |  | 203.8 | 136.2 | 121.3 | 203.2 | 197.3 | 217.4 | 205.9 |  |  |  | 203.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.52 | 4.76 | 5.23 | 5.08 | 5.33 | 4.68 | 4.98 |  |  |  | 4.89
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 6
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE |  | 2024-06-06
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK |  | OK |  |  | OK | OK
OPENING OF VANE |  | % | 0~100% | 71.3 | 71.7 | 76.7 | 77.7 |  | 70.8 |  | 73.5 |  |  | 77.3 | 71.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.8 | 0.8 | 0 | 0 |  | 0 |  | 0.1 |  |  | 0.3 | 0.3
OPENING OF 2nd VANE |  | % | 0~100% | 66.2 | 66.2 | 74.5 | 75.4 |  | 67.7 |  | 67.9 |  |  | 73.5 | 66.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 63.2 | 64.9 | 66.8 | 67 |  | 62.8 |  | 65.7 |  |  | 71.8 | 72.8
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 57.4 | 56.8 | 47.3 | 49.2 |  | 35.1 |  | 33.1 |  |  | 42 | 39.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  |  | 6.6 | 6.6
| CURRENT | A | ≤115A | 116 | 117 | 117.8 | 117.3 |  | 115.3 |  | 119.4 |  |  | 121 | 115.1
| INPUT | Kw | 1194kW | 1159 | 1159 | 1200 | 1204 |  | 1191 |  | 1216 |  |  | 1218 | 1171
COMPRESSOR | RUNNING TIME | Hr | NA | 45706.2 | 45697.9 | 46461 | 46452.7 |  | 44255.3 |  | 46468.5 |  |  | 47595.7 | 47586.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.1 | 59.2 | 59.5 |  | 57.7 |  | 57.5 |  |  | 59.4 | 59.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.53 | 0.49 | 0.49 |  | 0.59 |  | 0.54 |  |  | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.2 | 44.8 | 44.9 | 44.8 |  | 44.8 |  | 45 |  |  | 35.2 | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.24 | 0.23 | 0.22 | 0.22 |  | 0.28 |  | 0.23 |  |  | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.9 | 4.4 | 3.9 | 3.3 |  | 4.4 |  | 4.8 |  |  | 4.4 | 4.5
| SATURATION TEMPERATURE | CELCIUS | C | 3.9 | 4.1 | 2.9 | 2.8 |  | 3.8 |  | 3.5 |  |  | 3.2 | 3.7
| APPROACH TEMP | CELCIUS | C | 0.8 | 0.5 | 1.4 | 1.8 | 0 | 0.1 | 0 | 0.3 | 0 | 0 | 1.3 | 0.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 738.8 | 703.1 | 710 | 675.9 |  | 647.31 |  | 692.9 |  |  | 736.24 | 655.9
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.4 | 13.3 | 12.9 | 13.5 |  | 13.2 |  | 13.4 |  |  | 13.2 | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.7 | 4.9 | 5.3 | 5.1 |  | 4.5 |  | 5.1 |  |  | 5.7 | 5.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.7 | 8.4 | 7.6 | 8.4 |  | 8.7 |  | 8.3 | 0 | 0 | 7.5 | 8.2
| CHILLING CAPACITY | kW | 7032.6kW | 6614.8372 | 6819.9076 | 6274.4186 | 6556.0739 |  | 6502.9988 |  | 6640.9584 | 0 | 0 | 6376.2125 | 6210.6005
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.84 | 0.84 | 0.87 | 0.88 |  | 0.85 |  | 0.87 |  |  | 0.86 | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 37.8 | 37.2 | 37.9 | 37.9 |  | 37.2 |  | 38.2 |  |  | 37.3 | 37.3
| SATURATED TEMEPRATURE | CELCIUS | C | 37.1 | 37.4 | 38.6 | 38.7 |  | 37.8 |  | 38.6 |  |  | 37.4 | 37.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 3.4 | 1.9 | 3.5 | 3.3 |  | 2 |  | 2.9 | 0 | 0 | 2 | 2.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.8 | 29.7 | 29.2 | 29.4 |  | 29.6 |  | 29.6 |  |  | 29.5 | 29.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.4 | 35.3 | 34.4 | 34.6 |  | 35.2 |  | 35.3 |  |  | 35.3 | 35.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 5.6 | 5.2 | 5.2 |  | 5.6 |  | 5.7 | 0 | 0 | 5.8 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1196.72 | 1221.7 | 1229.6 | 1255.8 |  | 1290.2 |  | 1197 |  |  | 1197.56 | 1213.5
| HEAT CAPACITY | kW | 8226.9 | 7792.5953 | 7900.1386 | 7434.7907 | 7540.6005 |  | 8343.0947 |  | 7878.6374 | 0 | 0 | 8020.6097 | 7987.2402
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.48 | 0.47 | 0.47 |  | 0.47 |  | 0.49 |  |  | 0.48 | 0.48
| SATURATED TEMPERATURE | CELCIUS | C | 20.4 | 20.5 | 20.3 | 20.3 |  | 20 |  | 21.6 |  |  | 20.5 | 21
| LIQUID LEVEL | mm | mm | 204.1 | 217.7 | 120.5 | 122.5 |  | 202.1 |  | 207 |  |  | 203.1 | 196.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 4.98 | 5.47 | 4.77 | 5.02 |  | 5.45 |  | 5.04 |  |  | 4.61 | 5.26
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO
---

## 7
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK
OPENING OF VANE |  | % | 0~100% |  | 69.9 |  | 76.8 | 74.7 | 71.7 | 73.2 | 73.2 |  |  | 77.9 | 77.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.8 |  | 0 | 0 | 0 | 0.2 | 0.2 |  |  | 0.3 | 0.3
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.2 |  | 74.3 | 69.4 | 69.1 | 68.3 | 68.3 |  |  | 72.7 | 72.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 63.5 |  | 65.6 | 61.1 | 61.5 | 63.9 | 64.5 |  |  | 69.4 | 70.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 55 |  | 49.4 | 37.4 | 37.1 | 35.3 | 33.7 |  |  | 39.7 | 42.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  |  | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 113.9 |  | 114.3 | 117.2 | 114.1 | 117.2 | 116.7 |  |  | 117.5 | 117.4
| INPUT | Kw | 1194kW |  | 1131 |  | 1172 | 1207 | 1174 | 12.3 | 1191 |  |  | 1208 | 1194
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45722 |  | 46476.8 | 44273.9 | 4426.9 | 46487 | 46478.4 |  |  | 47620 | 47611.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 |  | 59 | 58 | 57.8 | 57.2 | 57.2 |  |  | 59.4 | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 | 0.59 | 0.58 | 0.54 | 0.53 |  |  | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45 |  | 45 | 45 | 45.2 | 45 | 45 |  |  | 45 | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.21 | 0.23 | 0.22 | 0.23 | 0.22 |  |  | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 |  | 3.1 | 4.5 | 3.8 | 4.5 | 4.3 |  |  | 4.2 | 3.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.4 |  | 2.3 | 3.5 | 3.1 | 3.5 | 3.3 |  |  | 3.2 | 3.7
| APPROACH TEMP | CELCIUS | C | 0 | 0.4 | 0 | 1.4 | 0.2 | 0.1 | 0.2 | 0.3 | 0 | 0 | 1 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 679.7 |  | 652 | 699.44 | 656.2 | 754.76 | 688.1 |  |  | 730.08 | 673.5
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.1 |  | 13.1 | 12.9 | 12.5 | 12.8 | 13.1 |  |  | 12.7 | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.4 |  | 4.5 | 4.7 | 3.9 | 4.7 | 4.6 |  |  | 5.2 | 4.8
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.7 | 0 | 8.6 | 8.2 | 8.6 | 8.1 | 8.5 | 0 | 0 | 7.5 | 8.4
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6828.3949 | 0 | 6474.8268 | 6622.873 | 6516.5358 | 7059.5335 | 6753.8684 | 0 | 0 | 6322.8637 | 6532.7945
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.81 |  | 0.84 | 0.84 | 0.82 | 0.85 | 0.84 |  |  | 0.82 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.9 |  | 36.5 | 36.5 | 36 | 37.4 | 37.1 |  |  | 36.7 | 36.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.2 |  | 37.5 | 37.2 | 36.6 | 37.8 | 37.4 |  |  | 36.8 | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 1.8 | 0 | 3.2 | 2 | 2 | 3 | 3 | 0 | 0 | 2.1 | 2.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.5 |  | 28.4 | 28.9 | 28.5 | 28.9 | 28.5 |  |  | 28.7 | 28.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.1 |  | 33.3 | 34.5 | 34 | 34.4 | 34.1 |  |  | 34.6 | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.6 | 0 | 4.9 | 5.6 | 5.5 | 5.5 | 5.6 | 0 | 0 | 5.9 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1219.3 |  | 1361.7 | 1295.7 | 1290.7 | 1228.54 | 1197 |  |  | 1240.88 | 1214.1
| HEAT CAPACITY | kW | 8226.9 | 0 | 7884.6189 | 0 | 7704.7691 | 8378.6605 | 8197.2864 | 7802.5058 | 7740.4157 | 0 | 0 | 8454.0323 | 8131.3857
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.46 | 0.46 | 0.45 | 0.48 | 0.47 |  |  | 0.47 | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.5 |  | 19.3 | 19.4 | 19 | 20.6 | 20.3 |  |  | 20.1 | 19.8
| LIQUID LEVEL | mm | mm |  | 206.9 |  | 123.4 | 2.8.7 | 201.8 | 203.6 | 215.3 |  |  | 195.4 | 198.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.75 |  | 5.41 | 5.08 | 5.46 | 4.8 | 5.3 |  |  | 4.65 | 5.19
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 8
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK |  |  |  | OK
OPENING OF VANE |  | % | 0~100% | 70.5 | 71.4 | 76.6 | 76.6 |  | 74.7 | 73.2 | 73.2 |  |  |  | 76.9
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.3 | 0.2 | 0 | 0 |  | 0 | 0.2 | 0.2 |  |  |  | 0.3
OPENING OF 2nd VANE |  | % | 0~100% | 66.2 | 66.2 | 72 | 72 |  | 69.4 | 68.3 | 68.3 |  |  |  | 72.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 64.1 | 63.7 | 67 | 65.9 |  | 62 | 63.7 | 64.6 |  |  |  | 71.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 56.3 | 53.8 | 46.2 | 48.7 |  | 36.5 | 30.6 | 34.7 |  |  |  | 39.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 118.8 | 117.9 | 117.2 | 117.6 |  | 118.3 | 118.9 | 119.4 |  |  |  | 119.3
| INPUT | Kw | 1194kW | 1163 | 1163 | 1184 | 1195 |  | 1213 | 1212 | 1214 |  |  |  | 1213
COMPRESSOR | RUNNING TIME | Hr | NA | 45740.3 | 45730 | 46495.3 | 46485 |  | 44288 | 46511.1 | 46501 |  |  |  | 47629
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.6 | 58.5 | 59.3 | 59.2 |  | 57.8 | 57.4 | 57.2 |  |  |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 | 0.49 | 0.49 |  | 0.59 | 0.54 | 0.54 |  |  |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.7 | 44.7 | 44.9 | 45 |  | 44.8 | 44.9 | 45 |  |  |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 | 0.22 | 0.22 |  | 0.23 | 0.23 | 0.23 |  |  |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.6 | 4.4 | 3.9 | 3.9 |  | 4.6 | 4.8 | 4.6 |  |  |  | 4.4
| SATURATION TEMPERATURE | CELCIUS | C | 4.1 | 3.8 | 2.9 | 2.9 |  | 3.6 | 3.5 | 3.6 |  |  |  | 3.7
| APPROACH TEMP | CELCIUS | C | 0.4 | 0.4 | 1.3 | 1.1 | 0 | -0.3 | 0.2 | 0.3 | 0 | 0 | 0 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 744.3 | 700 | 718.6 | 674 |  | 660 | 746 | 702 |  |  |  | 687
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13 | 13 | 12.9 | 13.2 |  | 13.1 | 13 | 13.3 |  |  |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5 | 4.8 | 5.2 | 5 |  | 4.3 | 5 | 4.9 |  |  |  | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8 | 8.2 | 7.7 | 8.2 | 0 | 8.8 | 8 | 8.4 | 0 | 0 | 0 | 8.2
| CHILLING CAPACITY | kW | 7032.6kW | 6875.7506 | 6628.1755 | 6389.3995 | 6381.9861 | 0 | 6706.6975 | 6891.455 | 6809.2379 | 0 | 0 | 0 | 6505.0808
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.84 | 0.83 | 0.87 | 0.87 |  | 0.85 | 0.87 | 0.86 |  |  |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 37.1 | 36.8 | 37.8 | 37.5 |  | 36.9 | 38 | 37.9 |  |  |  | 37.1
| SATURATED TEMEPRATURE | CELCIUS | C | 37.3 | 37 | 38.5 | 38.3 |  | 37.6 | 38.4 | 38.3 |  |  |  | 37.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.1 | 1.9 | 4.2 | 4.1 | 0 | 2.7 | 3.4 | 3.4 | 0 | 0 | 0 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.5 | 29.2 | 29.4 | 29.1 |  | 29.3 | 29.4 | 29.3 |  |  |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 35.2 | 35.1 | 34.3 | 34.2 |  | 34.9 | 35 | 34.9 |  |  |  | 34.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.7 | 5.9 | 4.9 | 5.1 | 0 | 5.6 | 5.6 | 5.6 | 0 | 0 | 0 | 5.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1214.1 | 1218 | 1255.8 | 1258 |  | 1288 | 1192.9 | 1197 |  |  |  | 1214
| HEAT CAPACITY | kW | 8226.9 | 7991.1894 | 8298.1524 | 7105.5658 | 7408.545 | 0 | 8328.8684 | 7713.903 | 7740.4157 | 0 | 0 | 0 | 8270.9007
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.48 | 0.47 | 0.48 | 0.47 |  | 0.47 | 0.49 | 0.48 |  |  |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C | 20.4 | 20.2 | 20.4 | 20.2 |  | 19.8 | 21 | 21 |  |  |  | 20.4
| LIQUID LEVEL | mm | mm | 180.5 | 196.4 | 128.6 | 128.4 |  | 205.3 | 218.3 | 208.2 |  |  |  | 196
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.06 | 5.22 | 4.85 | 4.98 |  | 5.35 | 4.83 | 5.01 |  |  |  | 4.92
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 9
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK | OK | OK |  |  |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.1 | 80.6 | 76.4 | 71.7 | 73.2 | 73.2 | 72.1 |  |  |  | 77.1
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0.2 |  |  |  | 0.3
OPENING OF 2nd VANE |  | % | 0~100% |  | 63.4 | 78.5 | 72.1 | 69.1 | 69.7 | 68.4 | 68.4 |  |  |  | 72.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 63.8 | 69.7 | 64.3 | 62.5 | 62.3 | 64.7 | 64.2 |  |  |  | 71
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 53.2 | 54.2 | 48.2 | 37.1 | 36.4 | 33.9 | 34.8 |  |  |  | 36.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  |  |  | 6.6
| CURRENT | A | ≤115A |  | 117.9 | 119.5 | 117.6 | 114.1 | 118.3 | 116.7 | 119.4 |  |  |  | 119.3
| INPUT | Kw | 1194kW |  | 1162 | 1228 | 1195 | 1174 | 1213 | 1191 | 1214 |  |  |  | 1213
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45755 |  | 46505.2 |  | 44302 |  | 46513 |  |  |  | 47641
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 | 59.2 | 59.1 | 57.8 | 57.3 | 57.2 | 57.3 |  |  |  | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.48 | 0.48 | 0.57 | 0.58 | 0.59 | 0.54 |  |  |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.1 | 46 | 46.1 | 45.3 | 45 | 45.1 | 45.3 |  |  |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.24 | 0.23 | 0.23 | 0.23 | 0.24 | 0.22 | 0.23 |  |  |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.5 | 3.8 | 3.8 | 3.8 | 4.5 | 4.3 | 4.5 |  |  |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.8 | 2.9 | 2.9 | 3.1 | 3.7 | 3.5 | 3.5 |  |  |  | 3.6
| APPROACH TEMP | CELCIUS | C | 0 | 0.2 | 1.5 | 1.1 | 0.8 | -0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0.4
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 712 | 709.2 | 681 | 656.2 | 687 | 688.1 | 710 |  |  |  | 688
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.2 | 13.6 | 13.3 | 13 | 13.2 | 13.4 | 13.3 |  |  |  | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 | 5.3 | 4.9 | 4.6 | 4.2 | 4.6 | 4.8 |  |  |  | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.5 | 8.3 | 8.4 | 8.4 | 9 | 8.8 | 8.5 | 0 | 0 | 0 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6988.4527 | 6797.1824 | 6605.5427 | 6364.9885 | 7139.7229 | 6992.2402 | 6968.8222 | 0 | 0 | 0 | 6752.8868
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.84 | 0.86 | 0.86 | 0.82 | 0.85 | 0.84 | 0.86 |  |  |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.5 | 37.1 | 37.2 | 36 | 36.8 | 37.1 | 37.8 |  |  |  | 37.2
| SATURATED TEMEPRATURE | CELCIUS | C |  | 37.2 | 38 | 38.1 | 36.6 | 37.8 | 37.4 | 38.4 |  |  |  | 37.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2 | 4.6 | 3 | 3 | 2.8 | 3.5 | 4.1 | 0 | 0 | 0 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.1 | 28.3 | 29.1 | 28.6 | 29.1 | 28.5 | 29.4 |  |  |  | 29.3
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 35.2 | 33.4 | 35.1 | 33.6 | 35 | 33.9 | 34.3 |  |  |  | 34.4
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 6.1 | 5.1 | 6 | 5 | 5.9 | 5.4 | 4.9 | 0 | 0 | 0 | 5.1
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1220 | 1233.1 | 1255 | 1290.1 | 1275 | 1191.5 | 1200 |  |  |  | 1211
| HEAT CAPACITY | kW | 8226.9 | 0 | 8593.5335 | 7261.9053 | 8695.1501 | 7448.6143 | 8686.4896 | 7429.6767 | 6789.8383 | 0 | 0 | 0 | 7131.7552
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.46 | 0.46 | 0.45 | 0.47 | 0.47 | 0.48 |  |  |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.1 | 19.9 | 20.1 | 19 | 19.9 | 20.4 | 20.8 |  |  |  | 20.3
| LIQUID LEVEL | mm | mm |  | 196.1 | 121.2 | 130.1 | 201.8 | 205 | 215.4 | 207.9 |  |  |  | 196
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.22 | 5.03 | 4.98 | 5.46 | 5.35 | 5.3 | 5.02 |  |  |  | 4.93
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 10
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK |  | OK |  |  | OK | OK
OPENING OF VANE |  | % | 0~100% | 71.1 | 68.2 | 82.4 | 73.2 |  | 74.7 |  | 73.2 |  |  | 75.7 | 75.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.3 | 0.3 | 0 | 0 |  | 0 |  | 0.2 |  |  | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% | 67.1 | 62.2 | 79.2 | 68.2 |  | 70.1 |  | 58.3 |  |  | 71.4 | 71.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 64.2 | 66.3 | 66.3 | 68.8 |  | 63.2 |  | 66.9 |  |  | 71.1 | 72.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 54.2 | 51.7 | 48.2 | 50 |  | 36.8 |  | 34.1 |  |  | 39.1 | 41.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 117.4 | 116.1 | 119.2 | 116.7 |  | 118.3 |  | 118.8 |  |  | 118.6 | 117.6
| INPUT | Kw | 1194kW | 1157.5 | 1139 | 1219 | 1175 |  | 1207 |  | 1204 |  |  | 1194 | 1196
COMPRESSOR | RUNNING TIME | Hr | NA | 45773.8 | 45764 | 46530 | 46520 |  | 44321 |  | 46549 |  |  | 47666.5 | 47656
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 60.2 | 59.3 | 58.9 |  | 58 |  | 57.3 |  |  | 59.3 | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.47 | 0.52 | 0.49 | 0.5 |  | 0.59 |  | 0.54 |  |  | 0.49 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.6 | 46.4 | 45.2 | 45 |  | 44.9 |  | 45 |  |  | 46 | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.28 | 0.23 | 0.21 | 0.23 |  | 0.23 |  | 0.23 |  |  | 0.25 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.5 | 4.8 | 3.5 | 4.2 |  | 4.5 |  | 4.7 |  |  | 4.4 | 4.4
| SATURATION TEMPERATURE | CELCIUS | C | 3.9 | 4.2 | 2.5 | 3.4 |  | 3.6 |  | 3.7 |  |  | 3.4 | 3.5
| APPROACH TEMP | CELCIUS | C | 0.3 | 0.4 | 1.3 | 1.2 | 0 | -0.2 | 0 | 0.4 | 0 | 0 | 0.9 | 0.5
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 746.32 | 730 | 715.44 | 699 |  | 660 |  | 703 |  |  | 733 | 642
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.4 | 13.2 | 12.5 | 13.3 |  | 13.2 |  | 13.3 |  |  | 12.7 | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.8 | 5.2 | 4.8 | 5.4 |  | 4.3 |  | 5.1 |  |  | 5.3 | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.6 | 8 | 7.7 | 7.9 | 0 | 8.9 | 0 | 8.2 | 0 | 0 | 7.4 | 8.5
| CHILLING CAPACITY | kW | 7032.6kW | 6549.6905 | 6743.649 | 6361.3025 | 6376.5589 | 0 | 6782.9099 | 0 | 6656.582 | 0 | 0 | 6263.5104 | 6301.3857
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.83 | 0.83 | 0.87 | 0.86 |  | 0.84 |  | 0.83 |  |  | 0.83 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.7 | 36.7 | 37.5 | 37.2 |  | 36.7 |  | 37.7 |  |  | 36.7 | 36.9
| SATURATED TEMEPRATURE | CELCIUS | C | 36.9 | 36.9 | 38.3 | 38.1 |  | 37.4 |  | 38.1 |  |  | 36.9 | 36.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.6 | 2 | 4.6 | 4.1 | 0 | 2.7 | 0 | 3.4 | 0 | 0 | 2.7 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.6 | 29.1 | 28.3 | 28.9 |  | 29.1 |  | 29 |  |  | 28.5 | 28.9
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.3 | 34.9 | 33.7 | 34 |  | 34.7 |  | 34.7 |  |  | 34.2 | 34.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.7 | 5.8 | 5.4 | 5.1 | 0 | 5.6 | 0 | 5.7 | 0 | 0 | 5.7 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1191.54 | 1218 | 1230.74 | 1256 |  | 1283 |  | 1190 |  |  | 1187.34 | 1211
| HEAT CAPACITY | kW | 8226.9 | 7842.6998 | 8157.5058 | 7674.3603 | 7396.7667 | 0 | 8296.5358 | 0 | 7832.5635 | 0 | 0 | 7815.0554 | 8110.6236
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.48 | 0.47 | 0.48 |  | 0.46 |  | 0.48 |  |  | 0.47 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 20.2 | 20.5 | 19.8 | 20.5 |  | 19.5 |  | 20 |  |  | 20.3 | 20.3
| LIQUID LEVEL | mm | mm | 206.6 | 215.1 | 125.8 | 117 |  | 207 |  | 218.1 |  |  | 202.6 | 201.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.04 | 5.24 | 4.94 | 4.96 |  | 5.45 |  | 5.14 |  |  | 4.82 | 5.19
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 11
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  |  | OK | OK | OK | OK | OK | OK |  |  |  | OK
OPENING OF VANE |  | % | 0~100% |  | 71.8 | 82.4 | 82.4 | 75.5 | 77.1 | 74.8 | 74.8 |  |  |  | 75.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.3 | 0 | 0 | 0 | 0 | 0.1 | 0.1 |  |  |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.6 | 79.1 | 79.2 | 70.9 | 73.1 | 69 | 69.1 |  |  |  | 42.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 71.8 | 50.4 | 82.4 | 62.7 | 75.5 | 65.8 | 74.8 |  |  |  | 75.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.5 | 68.2 | 79.1 | 36.8 | 69.7 | 31.9 | 69.1 |  |  |  | 71.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 115.6 | 121.4 | 118.1 | 118.8 | 118.2 | 119.4 | 118.9 |  |  |  | 117.3
| INPUT | Kw | 1194kW |  | 1144.3 | 1239 | 1215.3 | 1209 | 1200 | 1209 | 1210.9 |  |  |  | 1191.9
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45789 | 46678.3 | 46545 | 44343.9 | 44332 | 46709 | 46560 |  |  |  | 47682
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 45.1 | 59.7 | 45.1 | 57.8 | 46 | 57.5 | 45.1 |  |  |  | 44.9
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.46 | 0.59 | 0.53 | 0.53 | 0.58 |  |  |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 57.9 | 44.8 | 59.6 | 44.9 | 57.8 | 45 | 57.4 |  |  |  | 59.3
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.22 | 0.22 | 0.24 | 0.23 | 0.23 | 0.23 |  |  |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4 | 3.9 | 4.8 | 4.3 | 4 | 4.3 | 4 |  |  |  | 4
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.5 | 2.9 | 2.4 | 3.7 | 3.4 | 3.9
| APPROACH TEMP | CELCIUS | C | 0 | 0.5 | 1.8 | -0.4 | 0.1 | 0.4 | 0.3 | 0.6 | 0 | 0 | 0 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 686.64 | 713.76 | 659.84 | 700.32 | 654.96 | 745.08 | 689.92 |  |  |  | 675.68
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.7 | 13.7 | 12.8 | 13.4 | 13.2 | 13.4 | 13.2 |  |  |  | 13.1
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.5 | 5.7 | 4.4 | 4.4 | 4.4 | 4.6 | 4.6 |  |  |  | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.2 | 8 | 8.4 | 9 | 8.8 | 8.8 | 8.6 | 0 | 0 | 0 | 8
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6501.6721 | 6593.6259 | 6444.9488 | 7278.1524 | 6701.9163 | 7571.2517 | 6899.2 | 0 | 0 | 0 | 6285.3953
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.83 | 0.87 | 0.86 | 0.85 | 0.84 | 0.89 | 0.86 |  |  |  | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.6 | 37.7 | 38 | 37.5 | 37.1 | 37.6 | 37.9 |  |  |  | 36.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.5 | 38.6 | 38.1 | 38.4 | 37.4 | 39 | 33 |  |  |  | 36.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.7 | 4.2 | 4.7 | 3.6 | 3.5 | 4.3 | 4.1 | 0 | 0 | 0 | 2.7
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.3 | 29.1 | 28.2 | 29.2 | 28.3 | 29.1 | 28.1 |  |  |  | 28.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.8 | 34.4 | 33.3 | 34.8 | 33.6 | 34.7 | 33.8 |  |  |  | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 5.3 | 5.1 | 5.6 | 5.3 | 5.6 | 5.7 | 0 | 0 | 0 | 5.6
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1221.08 | 1287.28 | 1264.76 | 1298.8 | 1295.42 | 1215.2 | 1193.5 |  |  |  | 1213.38
| HEAT CAPACITY | kW | 8226.9 | 0 | 7755.127 | 7878.2725 | 7500.3209 | 8398.7067 | 7983.4023 | 7858.1062 | 7910.407 | 0 | 0 | 0 | 7901.0791
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.47 | 0.46 | 0.47 | 0.46 | 0.45 | 0.48 |  |  |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 | 20.1 | 19.8 | 19.8 | 19.5 | 20.7 | 24 |  |  |  | 20.2
| LIQUID LEVEL | mm | mm |  | 185.9 | 121.4 | 125.4 | 209.2 | 203.9 | 218.2 | 207.2 |  |  |  | 198.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.43 | 4.74 | 5.27 | 5.53 | 5.48 | 5.38 | 5.17 |  |  |  | 4.97
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 12
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK | OK | OK |  |  | OK | OK
OPENING OF VANE |  | % | 0~100% | 71.3 | 72.8 |  | 74.7 |  | 75.5 | 74.5 | 74.5 |  |  | 78.5 | 78.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.6 |  | 0 |  | 0 | 0.1 | 0.1 |  |  | 0.2 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% | 67.1 | 67.1 |  | 69.9 |  | 70.9 | 68.8 | 68.8 |  |  | 74 | 74
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 63.2 | 65.2 |  | 67.2 |  | 62.6 | 63.7 | 66.3 |  |  | 70.4 | 72.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 51.1 | 52.2 |  | 50.8 |  | 39.5 | 34.6 | 34 |  |  | 41.2 | 40.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 118.1 | 117.6 |  | 115.5 |  | 117.1 | 119.7 | 118.1 |  |  | 120.7 | 118.8
| INPUT | Kw | 1194kW | 1160 | 1160 |  | 1175 |  | 1190 | 1216 | 1205 |  |  | 1218 | 1210
COMPRESSOR | RUNNING TIME | Hr | NA | 45808 | 45798.8 |  | 46567.2 |  | 44356.4 | 46593 | 46583.9 |  |  | 47701 | 47691.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.2 | 58.1 |  | 59 |  | 57.8 | 57.5 | 57.3 |  |  | 59.4 | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  | 0.69 | 0.54 | 0.58 |  |  | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45 | 44.9 |  | 44.8 |  | 45 | 44.9 | 44.8 |  |  | 44.9 | 44.9
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.28 |  | 0.22 |  | 0.28 | 0.23 | 0.22 |  |  | 0.23 | 0.28
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.2 | 4 |  | 4 |  | 4 | 4.7 | 4.5 |  |  | 4.3 | 4.2
| SATURATION TEMPERATURE | CELCIUS | C | 3.8 | 3.8 |  | 2.9 |  | 3.3 | 3.6 | 3.4 |  |  | 3.3 | 3.2
| APPROACH TEMP | CELCIUS | C | 0.6 | 0.3 | 0 | 0.6 | 0 | 0.4 | 0.3 | -0.1 | 0 | 0 | 0.8 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 735 | 685.68 |  | 669.04 |  | 654.24 | 748 | 689.6 |  |  | 730 | 675.12
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.7 | 12.6 |  | 12.8 |  | 13.2 | 12.7 | 13.2 |  |  | 12.8 | 13
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.8 | 4.3 |  | 4.6 |  | 4.4 | 5 | 4.4 |  |  | 5.1 | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.9 | 8.3 | 0 | 8.2 | 0 | 8.8 | 7.7 | 8.8 | 0 | 0 | 7.7 | 8.1
| CHILLING CAPACITY | kW | 7032.6kW | 6704.9654 | 6571.7598 | 0 | 6335.0208 | 0 | 6648.1663 | 6650.8083 | 7007.4827 | 0 | 0 | 6490.7621 | 6314.6328
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.84 | 0.82 |  | 0.85 |  | 0.83 | 0.87 | 0.85 |  |  | 0.83 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.8 | 36 |  | 36.8 |  | 36.1 | 38.1 | 37.2 |  |  | 37.2 | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C | 37.2 | 36.4 |  | 37.6 |  | 36.9 | 38.4 | 37.6 |  |  | 37.4 | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2 | 2.5 | 0 | 3.8 | 0 | 3.6 | 3.3 | 4.2 | 0 | 0 | 2.2 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.4 | 28 |  | 27.9 |  | 27.9 | 29.3 | 27.8 |  |  | 29.2 | 28
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 35.2 | 33.5 |  | 33 |  | 33.3 | 35.1 | 33.4 |  |  | 35.2 | 33.8
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.8 | 5.5 | 0 | 5.1 | 0 | 5.4 | 5.8 | 5.6 | 0 | 0 | 6 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1211 | 1218.4 |  | 1258.74 |  | 1287.3 | 1193 | 1190.14 |  |  | 1207 | 1205.82
| HEAT CAPACITY | kW | 8226.9 | 8110.6236 | 7738.1062 | 0 | 7412.903 | 0 | 8027.0439 | 7990.0693 | 7696.0554 | 0 | 0 | 8362.5866 | 8075.9307
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.46 |  | 0.47 |  | 0.45 | 0.49 | 0.48 |  |  | 0.48 | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 20.2 | 19.7 |  | 19.8 |  | 19.3 | 21 | 20.4 |  |  | 20.4 | 19.9
| LIQUID LEVEL | mm | mm | 192.4 | 201.4 |  | 128.6 |  | 210.5 | 207.6 | 203.5 |  |  | 205.9 | 199.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.06 | 5.35 |  | 5.23 |  | 5.54 | 4.74 | 5.17 |  |  | 4.66 | 5.04
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 13
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  |  |  | OK
OPENING OF VANE |  | % | 0~100% | 69.4 | 70.1 | 69.9 | 76.8 | 63.7 | 62.8 |  | 73.9 |  |  |  | 77.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.6 | 0 | 0 | 0 | 0 |  | 0.1 |  |  |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% | 44.7 | 67.1 | 52.4 | 72.1 | 39.4 | 57.9 |  | 69.1 |  |  |  | 72.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 71.7 | 64.1 | 78.6 | 66.3 | 73.2 | 61.4 |  | 65.3 |  |  |  | 71.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 66.6 | 55.3 | 76.3 | 72.1 | 67.9 | 40.6 |  | 35.9 |  |  |  | 40.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 117.1 | 114.9 | 118.8 | 115.5 | 115.1 | 105.1 |  | 115.6 |  |  |  | 115.7
| INPUT | Kw | 1194kW | 1158 | 1124 | 1210 | 1169 | 1173 | 1068 |  | 1183 |  |  |  | 1180
COMPRESSOR | RUNNING TIME | Hr | NA | 45831 | 45823 | 46585 | 46577 | 44374 | 44366 |  | 46605 |  |  |  | 47715
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 57.8 | 59.1 | 58.7 | 57.4 | 57.9 |  | 57.3 |  |  |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.51 | 0.49 | 0.49 | 0.53 | 0.58 |  | 0.59 |  |  |  | 0.47
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.7 | 45.2 | 44.8 | 45.1 | 44.4 | 46.1 |  | 45.1 |  |  |  | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.24 | 0.22 | 0.22 | 0.21 | 0.23 | 0.28 |  | 0.22 |  |  |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.6 | 3.4 | 3.6 | 3.2 | 4.2 | 3.7 |  | 3.9 |  |  |  | 3.6
| SATURATION TEMPERATURE | CELCIUS | C | 3.9 | 3 | 2.9 | 2.4 | 3.5 | 2.9 |  | 2.8 |  |  |  | 2.8
| APPROACH TEMP | CELCIUS | C | 0 | 0.6 | 1.7 | 0.9 | 0.4 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 681.28 | 660.56 | 704.08 | 649.12 | 671.52 | 651.68 |  | 669.68 |  |  |  | 655.36
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.3 | 12.4 | 13.4 | 12.4 | 13.4 | 11.6 |  | 12.7 |  |  |  | 12.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.6 | 4 | 5.3 | 4.1 | 4.6 | 4 |  | 3.9 |  |  |  | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8.7 | 8.4 | 8.1 | 8.3 | 8.8 | 7.6 | 0 | 8.8 | 0 | 0 | 0 | 8.3
| CHILLING CAPACITY | kW | 7032.6kW | 6844.2679 | 6407.2794 | 6585.5058 | 6221.358 | 6823.7598 | 5719.1316 | 0 | 6805.0624 | 0 | 0 | 0 | 6281.164
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.81 | 0.79 | 0.85 | 0.83 | 0.82 | 0.79 |  | 0.82 |  |  |  | 0.89
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.8 | 35.1 | 36.7 | 35.9 | 35.8 | 35 |  | 36.6 |  |  |  | 35.5
| SATURATED TEMEPRATURE | CELCIUS | C | 36.1 | 35.5 | 37.5 | 36.9 | 36.5 | 35.4 |  | 36.7 |  |  |  | 35.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.8 | 1.9 | 4.6 | 4.3 | 3.3 | 0 | 0 | 3.4 | 0 | 0 | 0 | 2.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.7 | 27.7 | 27.5 | 27.6 | 27.2 | 27.7 |  | 27.7 |  |  |  | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.3 | 33.6 | 32.9 | 32.6 | 33.2 | 35.4 |  | 33.3 |  |  |  | 33.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.6 | 5.9 | 5.4 | 5 | 6 | 7.7 | 0 | 5.6 | 0 | 0 | 0 | 6
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1209.6 | 1220.1 | 1249.78 | 1259.58 | 1284.78 | 1288.98 |  | 1196.86 |  |  |  | 1210.72
| HEAT CAPACITY | kW | 8226.9 | 7821.8938 | 8312.4596 | 7793.0855 | 7272.4018 | 8901.4781 | 11460.9076 | 0 | 7739.5104 | 0 | 0 | 0 | 8388.3603
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.45 | 0.46 | 0.45 | 0.46 | 0.45 |  | 0.46 |  |  |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C | 19.6 | 18.9 | 19.5 | 19 | 19.2 | 18.9 |  | 19.7 |  |  |  | 19.2
| LIQUID LEVEL | mm | mm | 172 | 198.4 | 125.3 | 122.8 | 208.6 | 194.9 |  | 203.6 |  |  |  | 195.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.72 | 5.86 | 5.01 | 5.47 | 5.64 | 5.72 |  | 5.41 |  |  |  | 5.26
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 14
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK |  | OK | OK | OK |  |  | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 71.7 | 80.3 | 66.3 |  | 36.6 | 72.9 | 72.9 |  |  | 75.8 | 75.8
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0 | 0 |  | 0 | 0.1 | 0.1 |  |  | 0.2 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 66.6 | 76.7 | 62.2 |  | 27.4 | 67.7 | 67.7 |  |  | 71.3 | 71.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 63.5 | 68.2 | 59.7 |  | 50.4 | 66.3 | 65.8 |  |  | 73.2 | 71.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 53 | 47.7 | 51.7 |  | 16.9 | 30.6 | 31.6 |  |  | 38.8 | 40.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 114.7 | 117.7 | 106 |  | 81.5 | 116.8 | 116.2 |  |  | 117 | 116.3
| INPUT | Kw | 1194kW |  | 1145 | 1203 | 1087 |  | 829 | 1182 | 1185 |  |  | 1183 | 1180
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45846.9 | 46609.8 | 46601.1 |  | 44390.1 | 46623.9 | 46615.2 |  |  | 47733.9 | 47725.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 | 59.3 | 58.9 |  | 57.6 | 57.2 | 57.3 |  |  | 59.2 | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.49 |  | 0.58 | 0.53 | 0.59 |  |  | 0.49 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.8 | 44.8 | 45 |  | 45.2 | 45.9 | 44.9 |  |  | 45.1 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.22 | 0.22 | 0.21 |  | 0.22 | 0.22 | 0.22 |  |  | 0.22 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 3.6 | 3.4 | 3.3 |  | 4.3 | 4.2 | 4.3 |  |  | 4.2 | 3.9
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.2 | 2.7 | 2.3 |  | 3.4 | 3.2 | 3.4 |  |  | 3.2 | 3
| APPROACH TEMP | CELCIUS | C |  | 0.6 | 1.8 | 0.6 | 0 | -0.4 | 0.4 | 0.1 | 0 | 0 | 0.8 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 648.2 | 717.76 | 654.6 |  | 654.18 | 677.68 | 656.5 |  |  | 657.92 | 641.8
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.8 | 13 | 11.7 |  | 9.8 | 13.2 | 13.1 |  |  | 13.2 | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.2 | 5.2 | 3.9 |  | 3.9 | 4.6 | 4.4 |  |  | 5 | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8.6 | 7.8 | 7.8 | 0 | 5.9 | 8.6 | 8.7 | 0 | 0 | 8.2 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW |  | 6437.0901 | 6464.8129 | 5895.9353 | 0 | 4456.8845 | 6729.8476 | 6595.3233 | 0 | 0 | 6229.7275 | 6373.5335
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.87 | 0.84 |  | 0.77 | 0.86 | 0.85 |  |  | 0.83 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.2 | 37.3 | 36.4 |  | 34 | 38 | 38 |  |  | 36.6 | 36.6
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.5 | 38.5 | 37.2 |  | 34.6 | 37.9 | 37.7 |  |  | 36.8 | 36.7
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  |  | 1.8 | 4.6 | 3.9 | 0 | 2 | 4.1 | 3.3 | 0 | 0 | 2.8 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.8 | 28.6 | 28.8 |  | 28.9 | 28.3 | 28.9 |  |  | 28.6 | 28.7
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.7 | 33.9 | 33.3 |  | 32.6 | 33.8 | 34.4 |  |  | 34 | 34.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.9 | 5.3 | 4.5 | 0 | 3.7 | 5.5 | 5.5 | 0 | 0 | 5.4 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1221.5 | 1257.48 | 1254.2 |  | 1291 | 1203.72 | 1196.7 |  |  | 1212.54 | 1217.3
| HEAT CAPACITY | kW | 8226.9 |  | 8321.9977 | 7695.8938 | 6517.2055 | 0 | 5515.8199 | 7644.873 | 7600.2887 | 0 | 0 | 7560.873 | 8152.8176
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.47 | 0.46 |  | 0.48 | 0.45 | 0.48 |  |  | 0.47 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.6 | 20 | 19.5 |  | 20.5 | 20.5 | 28.5 |  |  | 20.1 | 20.1
| LIQUID LEVEL | mm | mm |  | 212.2 | 118 | 124.4 |  | 209.9 | 214.4 | 209.9 |  |  | 191.7 | 196.4
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.6 | 5.21 | 5.13 |  | 5.42 | 5.4 | 5.42 |  |  | 5.39 | 5.29
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 15
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 69.8 | 70.4 |  | 80.3 | 77.1 | 72.7 |  | 73 | 70.9 | 71.1 |  | 74.5
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0 |  | 0.3
OPENING OF 2nd VANE |  | % | 0~100% | 64.9 | 64.9 |  | 76.7 | 71.8 | 66.4 |  | 67.7 | 65.4 | 65.5 |  | 69.1
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 66.5 | 65.3 |  | 66 | 63.2 | 63.1 |  | 65.3 | 72.6 | 70 |  | 72.1
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 56 | 56.3 |  | 48.2 | 42.7 | 36 |  | 34.1 | 57.8 | 46.2 |  | 41.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 114.6 | 118.7 |  | 119.6 | 116.3 | 117.9 |  | 120.3 | 155.6 | 118.2 |  | 118.9
| INPUT | Kw | 1194kW | 1128 | 1161 |  | 1209 | 1194 | 1187 |  | 1210 | 1180 | 1201 |  | 1198
COMPRESSOR | RUNNING TIME | Hr | NA | 45865 | 45856.2 |  | 46624.5 | 44408 | 44399.4 |  | 46638.7 | 45984 | 45975.9 |  | 47743.8
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 58.2 |  | 59.6 | 57.4 | 57.8 |  | 57.3 | 58.7 | 58.7 |  | 59.6
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.49 | 0.58 | 0.59 |  | 0.54 | 0.48 | 0.49 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 44.7 |  | 44.8 | 44.9 | 44.8 |  | 45 | 44.9 | 45.1 |  | 44.7
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.23 |  | 0.22 | 0.22 | 0.23 |  | 0.23 | 0.23 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.2 | 4.4 |  | 3.6 | 4.2 | 4.7 |  | 4.9 | 5.1 | 5 |  | 4.8
| SATURATION TEMPERATURE | CELCIUS | C | 3.8 | 4.1 |  | 2.6 | 3.4 | 4 |  | 3.8 | 3.8 | 4.6 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0.3 | 0.6 | 0 | 1.6 | 0.4 | 0 | 0 | 0.2 | -0.3 | 0.2 | 0 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 734.16 | 709.1 |  | 686.4 | 700.08 | 673.9 |  | 715.3 | 768.16 | 722.5 |  | 700
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.4 | 13.2 |  | 13.1 | 13.1 | 13.2 |  | 13.3 | 12.4 | 13.4 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.5 | 5 |  | 5.2 | 4.6 | 4.7 |  | 5.1 | 4.8 | 5.2 |  | 5.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.9 | 8.2 | 0 | 7.9 | 8.5 | 8.5 | 0 | 8.2 | 7.6 | 8.2 | 0 | 7.8
| CHILLING CAPACITY | kW | 7032.6kW | 6697.3025 | 6714.3418 | 0 | 6261.6166 | 6871.455 | 6614.4919 | 0 | 6773.0485 | 6741.358 | 6841.224 | 0 | 6304.8499
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.79 | 0.84 |  | 0.87 | 0.81 | 0.85 |  | 0.87 | 0.85 | 0.85 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.1 | 36.9 |  | 37.9 | 34.9 | 37.3 |  | 38.8 | 35.7 | 37.5 |  | 37.3
| SATURATED TEMEPRATURE | CELCIUS | C | 35.6 | 37.3 |  | 38.6 | 36.3 | 37.9 |  | 38.4 | 36 | 37.9 |  | 37.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 23.2 | 2 | 0 | 4.1 | 2.7 | 2.7 | 0 | 3.4 | 2.4 | 2.3 | 0 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.9 | 29.7 |  | 29.5 | 27.9 | 29.7 |  | 29.6 | 27.6 | 29.5 |  | 29.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 33.4 | 35.3 |  | 34.5 | 33.6 | 35.2 |  | 35 | 33.6 | 35.6 |  | 35.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.5 | 5.6 | 0 | 5 | 5.7 | 5.5 | 0 | 5.4 | 6 | 6.1 | 0 | 5.8
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1297.6 | 1263.3 |  | 1302.1 | 1296.4 | 1286.9 |  | 1242.3 | 1152.34 | 1086.7 |  | 1259.6
| HEAT CAPACITY | kW | 8226.9 | 8241.1085 | 8169.1455 | 0 | 7517.8984 | 8532.8868 | 8173.1524 | 0 | 7746.4434 | 7983.8799 | 7654.5843 | 0 | 8436.1201
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.46 | 0.48 |  | 0.47 | 0.45 | 0.48 |  | 0.49 | 0.46 | 0.48 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C | 19.5 | 20.5 |  | 20.1 | 18.8 | 20.5 |  | 21.2 | 19.8 | 20.9 |  | 20.9
| LIQUID LEVEL | mm | mm | 212.7 | 218.9 |  | 134.6 | 198.1 | 207.1 |  | 218.5 | 155.6 | 159.1 |  | 200.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.41 | 5.15 |  | 4.86 | 5.42 | 5.33 |  | 5.05 | 4.85 | 4.99 |  | 4.84
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 16
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 70.5 | 74.7 | 74.6 |  | 74.5 | 74.2 | 71.7 |  | 73.3 | 77.7 | 79.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.8 | 0 | 0 |  | 0 | 0.2 | 0.1 |  | 0 | 0.1 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.1 | 69.3 | 69.3 |  | 69.1 | 68.9 | 66.8 |  | 67.3 | 73.8 | 75.3
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 68.5 | 51.7 | 70.4 |  | 63.1 | 67.9 | 67.2 |  | 74.4 | 73.9 | 73.2
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 49.9 | 70.2 | 48.3 |  | 38 | 33.7 | 33.4 |  | 45.5 | 39.8 | 41.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 115.9 | 116.7 | 116.3 |  | 117.7 | 118.1 | 115.8 |  | 118.5 | 118.1 | 119.2
| INPUT | Kw | 1194kW |  | 1135 | 1181 | 1180 |  | 1200 | 1197 | 1186 |  | 1210 | 1195 | 1216
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45873.7 | 46774.9 | 46634.2 |  | 44416.9 | 46808 | 46648.5 |  | 45995.9 | 47889.3 | 47754.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.1 | 59.1 | 58.9 |  | 57.6 | 57.2 | 57.3 |  | 59 | 59.3 | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.5 | 0.5 |  | 0.59 | 0.53 | 0.53 |  | 0.49 | 0.47 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 | 44.8 | 45.2 |  | 45 | 45 | 44.8 |  | 44.8 | 45.1 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.22 | 0.22 |  | 0.23 | 0.22 | 0.23 |  | 0.23 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.2 | 4.2 | 4 |  | 4.1 | 4.2 | 4.6 |  | 4.9 | 3.8 | 4.1
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 | 3.2 | 3.3 |  | 3.4 | 3.2 | 3.4 |  | 3.8 | 3.2 | 3.4
| APPROACH TEMP | CELCIUS | C | 0 | 0.5 | 1.2 | 1.2 | 0 | 0 | 0.3 | 0.1 | 0 | 0.2 | 0.8 | 0.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 667.9 | 692.64 | 684.4 |  | 664.2 | 718.2 | 658 |  | 696.6 | 703.76 | 645.3
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.6 | 13.3 | 13.7 |  | 13.9 | 13.4 | 13.4 |  | 13.4 | 13.4 | 13.5
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.7 | 5.4 | 5.2 |  | 4.1 | 4.5 | 4.7 |  | 5.1 | 4.6 | 4.9
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.9 | 7.9 | 8.5 | 0 | 9.8 | 8.9 | 8.7 | 0 | 8.3 | 8.8 | 8.6
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6864.0993 | 6318.5404 | 6717.552 | 0 | 7516.351 | 7381.0393 | 6610.3926 | 0 | 6676.4203 | 7151.3718 | 6408.291
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.85 | 0.86 |  | 0.84 | 0.82 | 0.85 |  | 0.84 | 0.82 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 | 36.8 | 37.1 |  | 36.6 | 37.4 | 38.1 |  | 37.1 | 36.1 | 36.8
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.7 | 37.6 | 38.1 |  | 37.4 | 37.3 | 37.7 |  | 37.4 | 36.3 | 36.9
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.1 | 4.1 | 4.3 | 0 | 2.7 | 3.4 | 3.3 | 0 | 2.2 | 2.4 | 2.2
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 29.2 | 28.3 | 29 |  | 29.1 | 28.5 | 29 |  | 28.8 | 28.4 | 28.8
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.6 | 33.5 | 33.8 |  | 34.7 | 33.9 | 34.4 |  | 35.2 | 33.9 | 34.7
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.4 | 5.2 | 4.8 | 0 | 5.6 | 5.4 | 5.4 | 0 | 6.4 | 5.5 | 5.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1266.3 | 1302.38 | 1297.9 |  | 1297.2 |  | 1245.6 |  | 1087.3 | 1263 | 1259.8
| HEAT CAPACITY | kW | 8226.9 | 0 | 7896.097 | 7820.2956 | 7193.903 | 0 | 8388.3603 | 0 | 7767.0208 | 0 | 8035.4734 | 8021.3626 | 8582.933
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 | 0.47 | 0.48 |  | 0.46 | 0.47 | 0.48 |  | 0.48 | 0.46 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.2 | 20.1 | 20.5 |  | 19.5 | 20.3 | 20.7 |  | 20.5 | 19.6 | 20.1
| LIQUID LEVEL | mm | mm |  | 213.4 | 119.4 | 123.9 |  | 199.8 | 214.4 | 216.4 |  | 155.5 | 201.8 | 201.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.82 | 4.95 | 5.21 |  | 5.38 | 5.54 | 5.43 |  | 5.06 | 5.51 | 5.25
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 17
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 71.7 | 73.5 |  | 74.7 |  | 75.1 | 74.2 | 74.2 |  | 72 | 77.8 | 77.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.3 | 0.3 |  | 0 |  | 0 | 0.2 | 0.2 |  | 0 | 0.1 | 0.1
OPENING OF 2nd VANE |  | % | 0~100% | 68.7 | 68.8 |  | 69.3 |  | 69.9 | 68.9 | 68.9 |  | 67.1 | 73.8 | 73.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 65.3 | 68.3 |  | 51.7 |  | 63.5 | 65 | 67.9 |  | 74.2 | 70.8 | 73.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 56.4 | 55.3 |  | 70.2 |  | 38.6 | 34.9 | 33.7 |  | 44.3 | 73.8 | 39.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 119.6 | 119.7 |  | 116.7 |  | 117.5 | 120.6 | 118.1 |  | 118 | 120.9 | 118.1
| INPUT | Kw | 1194kW | 1189 | 1168 |  | 1181 |  | 1194 | 1230 | 1197 |  | 1198 | 1227 | 1195
COMPRESSOR | RUNNING TIME | Hr | NA | 46034 | 46023.4 |  | 46774.9 |  | 44553.1 | 46819.3 | 46808 |  | 46129.1 | 47900.6 | 47889.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58 | 58 |  | 59.1 |  | 57.9 | 44.8 | 57.2 |  | 58.9 | 59.4 | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 |  | 0.5 |  | 0.59 | 0.53 | 0.53 |  | 0.48 | 0.48 | 0.47
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 44.9 |  | 44.8 |  | 44.8 | 44.8 | 45 |  | 44.7 | 45 | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.26 | 0.26 |  | 0.22 |  | 0.26 | 0.23 | 0.22 |  | 0.23 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.5 | 4 |  | 4.2 |  | 4.4 | 5 | 4.2 |  | 4.8 | 4.5 | 3.8
| SATURATION TEMPERATURE | CELCIUS | C | 4.1 | 3.7 |  | 3.2 |  | 3.5 | 3.9 | 3.2 |  | 3.2 | 3.7 | 3.2
| APPROACH TEMP | CELCIUS | C | 0.7 | 0.9 | 0 | 1.2 | 0 | -0.2 | 0.3 | 0.3 | 0 | 0.2 | 1 | 0.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 755.3 | 725.2 |  | 692.64 |  | 678.2 | 749.44 | 718.2 |  | 727.95 | 750.88 | 703.76
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.1 | 13.4 |  | 13.3 |  | 13.1 | 13.2 | 13.4 |  | 13.3 | 13.4 | 13.4
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5.2 | 4.9 |  | 5.4 |  | 4.2 | 5.3 | 4.5 |  | 5 | 5.5 | 4.6
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.9 | 8.5 | 0 | 7.9 | 0 | 8.9 | 7.9 | 8.9 | 0 | 8.3 | 7.9 | 8.8
| CHILLING CAPACITY | kW | 7032.6kW | 6890.1501 | 7118.0139 | 0 | 6318.5404 | 0 | 6969.9538 | 6836.6928 | 7381.0393 | 0 | 6976.888 | 6849.8291 | 7151.3718
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.83 | 0.82 |  | 0.85 |  | 0.83 | 0.86 | 0.82 |  | 0.83 | 0.84 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.8 | 35.9 |  | 36.8 |  | 36.2 | 38.3 | 37.4 |  | 36.6 | 37 | 36.1
| SATURATED TEMEPRATURE | CELCIUS | C | 37.1 | 36.4 |  | 37.6 |  | 36.9 | 38.2 | 37.3 |  | 36.9 | 37.2 | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.1 | 2.1 | 0 | 4.1 | 0 | 2.7 | 3.4 | 3.4 | 0 | 2.3 | 2.3 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.2 | 28.5 |  | 28.3 |  | 28.5 | 29.1 | 28.5 |  | 28.2 | 28.9 | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 35 | 34.3 |  | 33.5 |  | 34.2 | 34.8 | 33.9 |  | 34.6 | 34.9 | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.8 | 5.8 | 0 | 5.2 | 0 | 5.7 | 5.7 | 5.4 | 0 | 6.4 | 6 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1220.31 | 1267.42 |  | 1302.38 |  | 1298.3 | 1201.2 | 1245.2 |  | 1085.2 | 1194.21 | 1263
| HEAT CAPACITY | kW | 8226.9 | 8172.9769 | 8488.4942 | 0 | 7820.2956 | 0 | 8545.3926 | 7906.2818 | 7764.5266 | 0 | 8019.9538 | 8273.9723 | 8021.3626
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.46 |  | 0.47 |  | 0.46 | 0.49 | 0.47 |  | 0.47 | 0.48 | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 20.2 | 19.7 |  | 20.1 |  | 19.5 | 21.1 | 20.3 |  | 20.1 | 20.4 | 19.6
| LIQUID LEVEL | mm | mm | 198.4 | 205.3 |  | 119.4 |  | 200 | 216.2 | 214.4 |  | 167.5 | 204.5 | 201.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 4.92 | 5.51 |  | 4.95 |  | 5.48 | 4.82 | 5.54 |  | 5.13 |  | 5.51
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 18
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK |  | OK |  | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 73.5 | 81.1 | 75.9 |  | 75.4 |  | 75.5 | 73.7 | 73.1 |  | 78.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0 | 0 |  | 0 |  | 0.1 | 0 | 0 |  | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 68.2 | 78.1 | 71.3 |  | 69 |  | 69.7 | 67.8 | 67.4 |  | 73.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.9 | 66.4 | 71.4 |  | 69.6 |  | 68.1 | 70.8 | 76 |  | 74
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 56.9 | 52.1 | 56.2 |  | 39.3 |  | 37.5 | 55.1 | 50.7 |  | 45.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 118.2 | 119.9 | 117.2 |  | 117.8 |  | 118.8 | 118.6 | 117.5 |  | 118.1
| INPUT | Kw | 1194kW |  | 1159 | 1216 | 1186 |  | 1191 |  | 1204 | 1212 | 1187 |  | 1192
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45901.9 | 46795.3 | 46661.9 |  | 44436 |  | 46687.5 | 46149.7 | 46014.8 |  | 47789.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 | 59.3 | 59 |  | 58 |  | 57.7 | 58.6 | 58.6 |  | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.5 |  | 0.59 |  | 0.53 | 0.48 | 0.48 |  | 0.47
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 | 45 | 45 |  | 44.9 |  | 45 | 44.9 | 44.9 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.26 | 0.22 | 0.22 |  | 0.26 |  | 0.22 | 0.23 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 3.9 | 3.6 | 4.3 |  | 4 |  | 4.3 | 5.2 | 4.6 |  | 3.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.3 | 2.8 | 3.2 |  | 3.2 |  | 3.2 | 4 | 3.2 |  | 3.2
| APPROACH TEMP | CELCIUS | C |  | 0.3 | 1.8 | 1.1 | 0 | 0.2 | 0 | 0.2 | 0.2 | 0.1 | 0 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 632.9 | 734.4 | 649.6 |  | 649.1 |  | 650.8 | 768.8 | 636.3 |  | 636.3
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.7 | 13.2 | 13.9 |  | 13.1 |  | 13.6 | 13.3 | 13.8 |  | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.2 | 5.4 | 5.4 |  | 4.2 |  | 4.5 | 5.4 | 4.7 |  | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 9.5 | 7.8 | 8.5 | 0 | 8.9 |  | 9.1 | 7.9 | 9.1 |  | 9.1
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6942.8984 | 6614.6882 | 6375.9815 | 0 | 6670.8891 | 0 | 6838.6605 | 7013.3025 | 6686.2933 | 0 | 6686.2933
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.86 | 0.85 |  | 0.83 |  | 0.82 | 0.83 | 0.83 |  | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.2 | 37.2 | 36.2 |  | 35.4 |  | 36.7 | 36.6 | 35.7 |  | 35.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.5 | 38.1 | 37 |  | 36.1 |  | 36.6 | 37 | 36.1 |  | 35.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  |  | 2.1 | 4.3 | 4.3 | 0 | 2.8 | 0 | 3.5 | 2.5 | 2.3 | 0 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.7 | 28.8 | 27.4 |  | 27.7 |  | 27.6 | 28.5 | 27.3 |  | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.4 | 33.8 | 32.7 |  | 33.3 |  | 33.1 | 34.5 | 33.8 |  | 33.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.7 | 5 | 5.3 | 0 | 5.6 |  | 5.5 | 6 | 6.5 |  | 5.6
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1262.9 | 1300.8 | 1301.7 |  | 1294.3 |  | 1240.6 | 1169.9 | 1088.3 |  | 1265.1
| HEAT CAPACITY | kW | 8226.9 | 0 | 8312.3903 | 7510.3926 | 7966.5242 | 0 | 8369.6074 | 0 | 7879.0993 | 8105.5427 | 8168.5335 | 0 | 8180.7852
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.47 | 0.47 |  | 0.46 |  | 0.47 | 0.47 | 0.46 |  | 0.45
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.7 | 19.8 | 20.1 |  | 19.5 |  | 19.8 | 20.3 | 19.4 |  | 19.2
| LIQUID LEVEL | mm | mm |  | 197.1 | 121.2 | 133 |  | 211.5 |  | 206.8 | 157.6 | 161.6 |  | 193.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.86 | 4.83 | 5.41 |  | 5.55 |  | 5.49 | 4.76 | 5.71 |  | 5.5
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 19
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 70.2 | 68.6 |  | 75.2 |  | 73.5 |  | 73.1 |  | 71.9 | 77.3 | 77.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.3 | 0.3 |  | 0 |  | 0 |  | 0.2 |  | 0 | 0.3 | 0.3
OPENING OF 2nd VANE |  | % | 0~100% | 64.5 | 51.9 |  | 70.1 |  | 68.3 |  | 67.9 |  | 66.3 | 72.8 | 72.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 64.1 | 70.8 |  | 69.3 |  | 63.7 |  | 67.6 |  | 73.6 | 69.7 | 73.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 56.9 | 64.5 |  | 50.4 |  | 37.5 |  | 32.4 |  |  | 39.1 | 41.4
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 118.9 | 117.4 |  | 116.9 |  | 116.2 |  | 117.3 |  | 118.1 | 120.8 | 117.8
| INPUT | Kw | 1194kW | 1167 | 1150 |  | 1189 |  | 1188 |  | 1191 |  | 1202 | 1223 | 1197
COMPRESSOR | RUNNING TIME | Hr | NA | 46062.9 | 45912 |  | 46684 |  | 44446 |  | 46698 |  | 46037 | 47927.5 | 47799
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.6 |  | 59.2 |  | 58.2 |  | 57.2 |  | 58.9 | 59.4 | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.53 |  | 0.5 |  | 0.53 |  | 0.59 |  | 0.53 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.8 | 45 |  | 44.8 |  | 44.3 |  | 45 |  | 44.6 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.21 | 0.28 |  | 0.22 |  | 0.23 |  | 0.23 |  | 0.21 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.8 | 4.6 |  | 4.3 |  | 4.5 |  | 4.2 |  | 5 | 4.6 | 4
| SATURATION TEMPERATURE | CELCIUS | C | 4.4 | 4.2 |  | 3.3 |  | 3.6 |  | 3.5 |  | 3.7 | 3.9 | 3.4
| APPROACH TEMP | CELCIUS | C | 0.5 | 0 | 0 | 0.3 | 0 | 0.2 | 0 | 0.4 | 0 | -0.2 | 1 | 1.1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 762.3 | 706.96 |  | 680.16 |  | 664.72 |  | 700.64 |  | 709.44 | 746.1 | 689.36
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13 | 12.8 |  | 12.8 |  | 13.5 |  | 13.2 |  | 12.9 | 13.1 | 13.1
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5.3 | 4.6 |  | 4.6 |  | 4.7 |  | 4.6 |  | 4.8 | 5.6 | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.7 | 8.2 | 0 | 8.2 | 0 | 8.8 |  | 8.6 | 0 | 8.1 | 7.5 | 8
| CHILLING CAPACITY | kW | 7032.6kW | 6777.9561 | 6694.0785 | 0 | 6440.3141 | 0 | 6754.6605 | 0 | 6957.8568 | 0 | 6635.6397 | 6461.6051 | 6368.2217
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.84 | 0.82 |  | 0.85 |  | 0.83 |  | 0.84 |  | 0.83 | 0.86 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.9 | 36.3 |  | 37.1 |  | 36.3 |  | 37.5 |  | 36.8 | 37.3 | 36.4
| SATURATED TEMEPRATURE | CELCIUS | C | 37.8 | 36.5 |  | 37.8 |  | 37 |  | 37.4 |  | 37.1 | 37.4 | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.5 | 3.1 | 0 | 4.9 | 0 | 3.7 | 0 | 4.2 | 0 | 3.4 | 2.1 | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 29.3 | 28.1 |  | 27.8 |  | 27.9 |  | 27.7 |  | 27.9 | 29.1 | 28.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 35.3 | 33.4 |  | 32.9 |  | 33.3 |  | 33.2 |  | 33.7 | 35.3 | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 6 | 5.3 | 0 | 5.1 | 0 | 5.4 |  | 5.5 | 0 | 5.8 | 6.2 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1190 | 1265.6 |  | 1298.22 |  | 133.32 |  | 1237.74 |  | 1078.98 | 1199 | 1254.82
| HEAT CAPACITY | kW | 8226.9 | 8244.8037 | 7745.5889 | 0 | 7645.4065 | 0 | 831.3256 | 0 | 7860.9353 | 0 | 7226.4249 | 8584.0647 | 7969.4111
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.48 | 0.47 |  | 0.47 |  | 0.48 |  | 0.47 |  | 0.48 | 0.48 | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 20.5 | 20.2 |  | 20.2 |  | 19.6 |  | 21.2 |  | 20.1 | 20.7 | 19.8
| LIQUID LEVEL | mm | mm | 176 | 215.3 |  | 135 |  | 200.1 |  | 200.4 |  | 159 | 193.7 | 196.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 4.85 | 5.37 |  | 4.91 |  | 5.46 |  | 5.53 |  | 5.03 | 4.54 | 5.32
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 20
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK |  | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.5 | 82.3 | 73.1 |  | 72.6 | 77.4 | 71.9 |  | 71.9 |  | 77.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.3 | 0 | 0 |  | 0 | 0.1 | 0.1 |  | 0 |  | 0.3
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.2 | 80.3 | 68.3 |  | 67.4 | 73.7 | 65.5 |  | 64.8 |  | 72.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 66.5 | 65.3 | 69 |  | 62.7 | 64.6 | 67.2 |  | 72.3 |  | 72.6
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 57.9 | 55 | 48.3 |  | 35.1 | 37.9 | 34.8 |  | 46.7 |  | 39
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 119.3 | 117.6 | 115.2 |  | 116.6 | 118.8 | 118.3 |  | 118 |  | 120.1
| INPUT | Kw | 1194kW |  | 1153 | 1203 | 1175 |  | 1195 | 1221 | 1203 |  | 1201 |  | 1219
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45935.5 | 46703.3 | 46693.2 |  | 44455.4 | 46717.1 | 46707 |  | 46046.6 |  | 47823.1
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.8 | 59.1 | 59.6 |  | 57.9 | 57.1 | 57.6 |  | 58.9 |  | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 | 0.48 | 0.5 |  | 0.59 | 0.59 | 0.54 |  | 0.58 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.2 | 44.7 | 45.6 |  | 44.9 | 45 | 44.8 |  | 45.6 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.28 | 0.21 | 0.23 |  | 0.23 | 0.22 | 0.23 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 | 3.1 | 4.1 |  | 4.3 | 4.4 | 4.2 |  | 5.2 |  | 4.5
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.2 | 2.3 | 3.4 |  | 3.8 | 3.4 | 3.9 |  | 3.7 |  | 3.8
| APPROACH TEMP | CELCIUS | C |  | 0.4 | 1.9 | 1.1 | 0 | 0.3 | 0.4 | 0.8 | 0 | 0 |  | 1
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 728.48 | 726 | 699.92 |  | 657.28 | 748.8 | 721.6 |  | 728 |  | 709.44
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.9 | 12.9 | 13 |  | 13.2 | 13 | 13.3 |  | 13 |  | 13.2
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 | 5 | 5.2 |  | 4.6 | 4.8 | 5 |  | 5.2 |  | 5.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 7.9 | 7.9 | 7.8 | 0 | 8.6 | 8.2 | 8.3 | 0 | 7.8 |  | 7.7
| CHILLING CAPACITY | kW | 7032.6kW |  | 6645.4873 | 6622.8637 | 6304.1293 | 0 | 6527.261 | 7090.254 | 6916.0277 | 0 | 6557.0439 |  | 6307.9538
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.84 | 0.83 | 0.87 |  | 0.85 | 0.82 | 0.87 |  | 0.85 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.8 | 35.8 | 37.3 |  | 36.9 | 36.4 | 38.5 |  | 37.4 |  | 37.1
| SATURATED TEMEPRATURE | CELCIUS | C |  | 37.1 | 36.8 | 38.2 |  | 37.5 | 36.5 | 38.2 |  | 37.7 |  | 37.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  |  | 2.8 | 4.4 | 4.5 | 0 | 3.5 | 3.6 | 5 | 0 | 3 |  | 2.8
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.8 | 27.1 | 28.7 |  | 28.8 | 27.1 | 27.7 |  | 28.7 |  | 29
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.3 | 32.4 | 33.7 |  | 34 | 32.9 | 33.2 |  | 34.7 |  | 34.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.5 | 5.3 | 5 | 0 | 5.2 | 5.8 | 5.5 | 0 | 6 |  | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1261.26 | 1263.3 | 1304.66 |  | 1296.26 | 1204.7 | 1237.74 |  | 1079.54 |  | 1254.96
| HEAT CAPACITY | kW | 8226.9 |  | 8010.3118 | 7731.5127 | 7532.679 | 0 | 7783.5473 | 8068.4296 | 7860.9353 | 0 | 7479.4919 |  | 7970.3002
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.48 | 0.44 | 0.48 |  | 0.47 | 0.46 | 0.47 |  | 0.48 |  | 0.48
| SATURATED TEMPERATURE | CELCIUS | C |  | 20.4 | 18.7 | 20.6 |  | 20.1 | 19.6 | 21.2 |  | 20.8 |  | 20.5
| LIQUID LEVEL | mm | mm |  | 197.9 | 131.2 | 119 |  | 213 | 211.5 | 200.4 |  | 157.5 |  | 208.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.37 | 4.9 | 5.1 |  | 5.4 | 4.91 | 4.93 |  | 4.82 |  | 4.77
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 21
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK |  | OK |  | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% |  | 70.5 |  | 75.7 | 74.7 | 74.7 |  | 69.8 | 73.4 | 73.4 |  | 76.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.3 |  | 0 | 0 | 0 |  | 0.1 | 0 | 0 |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 64.6 |  | 70.6 | 70.3 | 70.3 |  | 64.4 | 67.8 | 67.8 |  | 71.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 65.9 |  | 68 | 63.8 | 63.4 |  | 67.1 | 76.2 | 72.2 |  | 72.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 42.3 |  | 52.4 | 37.9 | 37.2 |  | 31 | 47.4 | 67.8 |  | 40.1
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 116.5 |  | 115.5 | 116.4 | 117.8 |  | 114.9 | 118.2 | 155.5 |  | 117.7
| INPUT | Kw | 1194kW |  | 1148 |  | 1179 | 1199 | 1211 |  | 1175 | 1208 | 12.4 |  | 1198
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45946 |  | 46714 | 44474 | 44466 |  | 46731 | 46065 | 46057 |  | 47833
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.1 | 57.8 | 58.1 |  | 57.4 | 58.5 | 58.6 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.53 |  | 0.49 | 0.59 | 0.59 |  | 0.54 | 0.5 | 0.58 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 |  | 45 | 45 | 44.8 |  | 44.9 | 45.1 | 45.2 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.28 |  | 0.22 | 0.23 | 0.28 |  | 0.23 | 0.24 | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.7 |  | 4 | 4.5 | 4.7 |  | 4.8 | 5.3 | 4.7 |  | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 4.1 |  | 3 | 3.5 | 3.6 |  | 3.7 | 4.2 | 3.7 |  | 3.5
| APPROACH TEMP | CELCIUS | C |  | 0.1 | 0 | 1 | 0 | 0 | 0 | -0.1 | 0 | 0.1 |  | 0.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 720.08 |  | 690.24 | 657.6 | 674.08 |  | 707.92 | 728.56 | 723.04 |  | 698.24
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.8 |  | 13.1 | 13.5 | 13.4 |  | 13.1 | 13.4 | 12.8 |  | 13
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 |  | 5 | 4.5 | 4.7 |  | 4.7 | 5.3 | 4.8 |  | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8 | 0 | 8.1 | 9 | 8.7 | 0 | 8.4 | 8.1 | 8 |  | 7.9
| CHILLING CAPACITY | kW | 7032.6kW |  | 6652.0092 | 0 | 6456.0554 | 6834.1801 | 6771.9353 | 0 | 6866.6605 | 6814.4758 | 6679.3533 |  | 6369.6259
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.87 |  | 0.85 | 0.83 | 0.84 |  | 0.84 | 0.82 | 0.85 |  | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.3 |  | 37 | 36.1 | 36.4 |  | 37.7 | 36.1 | 36.8 |  | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.5 |  | 37.8 | 36.9 | 37.2 |  | 37.5 | 36.6 | 37.2 |  | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  |  | 2.1 | 0 | 4.3 | 3.4 | 2.7 | 0 | 3.4 | 3.3 | 2.4 |  | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.9 |  | 28.7 | 27.9 | 28.8 |  | 28.7 | 27.8 | 28.7 |  | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.4 |  | 33.5 | 33.5 | 34.5 |  | 34.1 | 33.3 | 34.8 |  | 34.3
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.5 | 0 | 4.8 | 5.6 | 5.7 | 0 | 5.4 | 5.5 | 6.1 |  | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1264.48 |  | 1296.26 | 1281.14 | 1297.24 |  | 1240 | 1225.98 | 1077.58 |  | 1256.64
| HEAT CAPACITY | kW | 8226.9 |  | 8030.7621 | 0 | 7184.8129 | 8284.5081 | 8538.4157 | 0 | 7732.1016 | 7786.2471 | 7590.3441 |  | 8271.1871
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.47 |  | 0.47 | 0.46 | 0.46 |  | 0.48 | 0.47 | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 20 |  | 20.2 | 19.4 | 19.4 |  | 20.8 | 20.5 | 20.2 |  | 20.1
| LIQUID LEVEL | mm | mm |  | 182.8 |  | 124.7 | 208.1 | 206.7 |  | 114.9 | 162.3 | 155.5 |  | 201.9
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.4 |  | 5.12 | 5.52 | 5.29 |  | 5.1 | 5.19 | 5.11 |  | 4.97
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 22
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK |  | OK |  | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 71.4 | 80.3 | 76.4 |  | 74.7 |  | 73.7 |  | 73.4 | 82.5 | 77.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.4 | 0 | 0 |  | 0 |  | 0.1 |  | 0 | 0.1 | 0.1
OPENING OF 2nd VANE |  | % | 0~100% |  | 65.7 | 77.8 | 72 |  | 70.3 |  | 68.3 |  | 67.9 | 79.4 | 72.2
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 65.4 | 62.6 | 66.9 |  | 62.7 |  | 65.2 |  | 71.1 | 67.5 | 72.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 41.7 | 55 | 50.9 |  | 41.4 |  | 35.9 |  | 49.9 | 42.4 | 43.9
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 117.3 | 115.8 | 117 |  | 118 |  | 118.1 |  | 118.3 | 119.2 | 118.6
| INPUT | Kw | 1194kW |  | 1146 | 1183 | 1183 |  | 1205 |  | 1202 |  | 1204 | 1213 | 1201
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45955.3 | 46732.3 | 46723.3 |  | 44489.6 |  | 46740.9 |  | 46080.8 | 47851.7 | 47842.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 | 58.9 | 59.1 |  | 57.9 |  | 57.2 |  | 58.6 | 59 | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.48 | 0.49 |  | 0.59 |  | 0.53 |  | 0.58 | 0.47 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 | 45 | 44.8 |  | 44.8 |  | 45 |  | 44.8 | 45 | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.21 | 0.22 |  | 0.23 |  | 0.23 |  | 0.23 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 | 2.9 | 3.8 |  | 4.6 |  | 4.6 |  | 4.8 | 3.5 | 4.3
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 | 2 | 2.9 |  | 3.7 |  | 3.6 |  | 3.6 | 2.8 | 3.6
| APPROACH TEMP | CELCIUS | C |  | 0.2 | 1.1 | 1.4 | 0 | -0.2 | 0 | 0.4 | 0 | 0.2 | 0.8 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 719.1 | 719.28 | 689.3 |  | 674.6 |  | 714.4 |  | 722.5 | 734.64 | 699.7
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.3 | 11.7 | 13.1 |  | 13.2 |  | 13.1 |  | 13.2 | 11.9 | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 | 4 | 5.2 |  | 4.4 |  | 5 |  | 5 | 4.3 | 5.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 8.5 | 7.7 | 7.9 | 0 | 8.8 | 0 | 8.1 | 0 | 8.2 | 7.6 | 8.1
| CHILLING CAPACITY | kW | 7032.6kW |  | 7058.1409 | 6395.4457 | 6288.0716 | 0 | 6855.0577 | 0 | 6682.0323 | 0 | 6841.224 | 6447.1871 | 6544.5381
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.83 | 0.85 |  | 0.83 |  | 0.84 |  | 0.86 | 0.8 | 0.84
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.1 | 36 | 36.7 |  | 36.2 |  | 37.7 |  | 36.7 | 35.3 | 36.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 | 37 | 37.6 |  | 37 |  | 37.5 |  | 37 | 2.7 | 36.4
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  |  | 2.2 | 4.8 | 4.1 | 0 | 2.7 | 0 | 3.5 | 0 | 2.2 | 2.6 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.7 | 27 | 28.4 |  | 28.5 |  | 28.6 |  | 28.3 | 26.8 | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.2 | 32.2 | 33.5 |  | 34.3 |  | 34 |  | 34.8 | 32.7 | 34.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.5 | 5.2 | 5.1 | 0 | 5.8 | 0 | 5.4 | 0 | 6.5 | 5.9 | 5.7
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1265.6 | 1231.16 | 1304.3 |  | 1298.7 |  | 1239.4 |  | 1078.6 | 1191.26 | 1261.9
| HEAT CAPACITY | kW | 8226.9 |  | 8037.8753 | 7392.6467 | 7681.2125 | 0 | 8697.9908 | 0 | 7728.3603 | 0 | 8095.7275 | 8115.9746 | 8305.8083
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.45 | 0.46 |  | 0.46 |  | 0.48 |  | 0.47 | 0.45 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.8 | 18.7 | 19.8 |  | 19.4 |  | 20.8 |  | 20.1 | 18.8 | 20
| LIQUID LEVEL | mm | mm |  | 187.8 | 118.5 | 124.6 |  | 200.4 |  | 214.1 |  | 160.5 | 205.4 | 204.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.52 | 5.04 | 4.96 |  | 5.35 |  | 5.2 |  | 4.93 | 4.84 | 5.09
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 23
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  | OK | OK | OK |  | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 74.9 | 71.9 |  | 80.6 |  | 73.9 | 74.9 | 74.9 |  | 70 |  | 79.3
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.3 | 0.3 |  | 0 |  | 0 | 0.2 | 0.2 |  | 0 |  | 0.2
OPENING OF 2nd VANE |  | % | 0~100% | 69.5 | 66.2 |  | 77.8 |  | 68.7 | 69.2 | 69.2 |  | 63.7 |  | 74.6
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 65.9 | 65.9 |  | 67.2 |  | 63.1 | 66.3 | 66.6 |  | 72.3 |  | 72.3
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 55.2 | 51.1 |  | 53.8 |  | 39.9 | 38.9 | 37.7 |  | 51.5 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 118.8 | 117.7 |  | 118.6 |  | 115.9 | 119.4 | 119.1 |  | 115.6 |  | 119.6
| INPUT | Kw | 1194kW | 1159 | 1153 |  | 1198 |  | 1182 | 1202 | 1207 |  | 1174 |  | 1212
COMPRESSOR | RUNNING TIME | Hr | NA | 45972.5 | 45964.6 |  | 46747.9 |  | 44499.2 | 46758.6 | 46750.8 |  | 46090.7 |  | 47862
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58.2 |  | 59.1 |  | 57.9 | 56.8 | 57.1 |  | 58.7 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  | 0.59 | 0.53 | 0.53 |  | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.3 | 45.2 |  | 45.1 |  | 45 | 44.9 | 45.1 |  | 45.1 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.25 | 0.23 |  | 0.21 |  | 0.23 | 0.23 | 0.23 |  | 0.23 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.2 | 4.2 |  | 3.1 |  | 4.3 | 4.6 | 4.4 |  | 4.8 |  | 4.1
| SATURATION TEMPERATURE | CELCIUS | C | 3.4 | 3.8 |  | 2.4 |  | 3.5 | 3.6 | 3.5 |  | 3.8 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0.4 | 0.5 | 0 | 1.7 | 0 | -0.1 | 0 | 0.4 | 0 | 0.2 | 0 | 0.9
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 748.48 | 710.5 |  | 686 |  | 660.5 | 750.16 | 712.4 |  | 717.9 |  | 692.8
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.4 | 13.3 |  | 13.3 |  | 13.1 | 12.8 | 13.3 |  | 13.3 |  | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.6 | 4.7 |  | 4.8 |  | 4.2 | 4.6 | 4.8 |  | 5 |  | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.8 | 8.6 | 0 | 8.5 | 0 | 8.9 | 8.2 | 8.5 | 0 | 8.3 | 0 | 8.3
| CHILLING CAPACITY | kW | 7032.6kW | 6741.5058 | 7055.7737 | 0 | 6733.2564 | 0 | 6788.0485 | 7103.1316 | 6992.3788 | 0 | 6880.5658 | 0 | 6640
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.78 | 0.8 |  | 0.84 |  | 0.82 | 0.81 | 0.83 |  | 0.82 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 34.7 | 35.5 |  | 36.4 |  | 35.8 | 36 | 37.1 |  | 36.1 |  | 36
| SATURATED TEMEPRATURE | CELCIUS | C | 35.1 | 36 |  | 37.4 |  | 36.5 | 36.3 | 37.1 |  | 36.5 |  | 36.2
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.2 | 2.2 | 0 | 4.5 | 0 | 2.8 | 3.5 | 3.5 | 0 | 2.4 | 0 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 26.9 | 28.3 |  | 28.1 |  | 28.1 | 27 | 28.1 |  | 28 |  | 28
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 32.9 | 33.8 |  | 32.9 |  | 33.7 | 32.8 | 33.6 |  | 34.1 |  | 33.9
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 6 | 5.5 | 0 | 4.8 | 0 | 5.6 | 5.8 | 5.5 | 0 | 6.1 | 0 | 5.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1226.96 | 1263.2 |  | 1309.7 |  | 1295.4 | 1204.98 | 1241.6 |  | 1079.4 |  | 1258.8
| HEAT CAPACITY | kW | 8226.9 | 8500.8776 | 8022.6328 | 0 | 7259.3072 | 0 | 8376.7206 | 8070.3048 | 7885.4503 | 0 | 7603.164 | 0 | 8576.1201
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.46 |  | 0.45 |  | 0.45 | 0.47 | 0.47 |  | 0.47 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C | 18.9 | 19.6 |  | 19.2 |  | 19.3 | 19.8 | 20.2 |  | 20.1 |  | 19.7
| LIQUID LEVEL | mm | mm | 230.6 | 192 |  | 127 |  | 204.5 | 192.5 | 199.1 |  | 151.8 |  | 197.8
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.22 | 5.35 |  | 5.15 |  | 5.56 | 5.04 | 5.18 |  | 5.13 |  | 5.01
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 24
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 73.5 | 79.4 | 75.9 | 77.7 | 75.4 |  | 75.5 |  |  | 77.2 | 78.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0.5 | 0 | 0 | 0 |  | 0.1 |  |  | 0 | 0
OPENING OF 2nd VANE |  | % | 0~100% |  | 68.2 | 75.4 | 71.3 | 72.5 | 69 |  | 69.7 |  |  | 72.2 | 73.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.9 | 69.7 | 71.4 | 64.2 | 69.6 |  | 68.1 |  |  | 74.6 | 74
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 56.9 | 56.9 | 56.2 | 41.3 | 39.3 |  | 37.5 |  |  | 46.3 | 45.2
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 118.2 | 116.9 | 117.2 | 116.4 | 117.8 |  | 118.8 |  |  | 118.5 | 118.1
| INPUT | Kw | 1194kW |  | 1159 | 1208 | 1186 | 1207 | 1191 |  | 1204 |  |  | 1207 | 1192
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45982.9 | 46765.4 | 46756.3 | 44516.7 | 44507.7 |  | 46773.7 |  |  | 47879.7 | 47870.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58 | 59.3 | 59 | 57.3 | 58 |  | 57.7 |  |  | 59.3 | 59.1
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.5 | 0.59 | 0.59 |  | 0.53 |  |  | 0.48 | 0.47
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 44.9 | 45 | 45 | 44.8 | 44.9 |  | 45 |  |  | 44.9 | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.26 | 0.22 | 0.22 | 0.22 | 0.26 |  | 0.22 |  |  | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 3.9 | 4.1 | 4.3 | 4.3 | 4 |  | 4.3 |  |  | 4.8 | 3.8
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.3 | 3.1 | 3.2 | 3.4 | 3.2 |  | 3.2 |  |  | 3.2 | 3.2
| APPROACH TEMP | CELCIUS | C |  | 0.3 | 501.9 | 1.1 | -0.2 | 0.2 | 0 | 0.2 | 0 | 0 | 0.9 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 632.9 | 725.9 | 649.6 | 647.3 | 649.1 |  | 650.8 |  |  | 721.5 | 636.3
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13.7 | 13.9 | 13.9 | 13.3 | 13.1 |  | 13.6 |  |  | 13.8 | 13.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.2 | 506 | 5.4 | 4.1 | 4.2 |  | 4.5 |  |  | 5.7 | 4.5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 |  | 9.5 | -492.1 | 8.5 | 9.2 | 8.9 |  | 9.1 | 0 | 0 | 8.1 | 9.1
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6942.8984 | -412488.903 | 6375.9815 | 6876.6282 | 6670.8891 | 0 | 6838.6605 | 0 | 0 | 6748.4411 | 6686.2933
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.84 | 0.85 | 0.82 | 0.83 |  | 0.82 |  |  | 0.81 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.2 | 36.6 | 36.2 | 35.7 | 35.4 |  | 36.7 |  |  | 35.9 | 35.3
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.5 | 37.5 | 37 | 36.5 | 36.1 |  | 36.6 |  |  | 36.1 | 35.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  |  | 2.1 | 4.5 | 4.3 | 2.8 | 2.8 | 0 | 3.5 | 0 | 0 | 2.4 | 2.4
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.7 | 27.6 | 27.4 | 28 | 27.7 |  | 27.6 |  |  | 27.7 | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.4 | 33 | 32.7 | 33.7 | 33.3 |  | 33.1 |  |  | 33.7 | 33.1
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 |  | 5.7 | 5.4 | 5.3 | 5.7 | 5.6 |  | 5.5 | 0 | 0 |  | 5.6
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1262.9 | 1259.3 | 1301.7 | 1288.4 | 1294.3 |  | 1240.6 |  |  | 1213.8 | 1265.1
| HEAT CAPACITY | kW | 8226.9 | 0 | 8312.3903 | 7852.448 | 7966.5242 | 8480.2309 | 8369.6074 | 0 | 7879.0993 | 0 | 0 | 0 | 8180.7852
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.46 | 0.47 | 0.45 | 0.46 |  | 0.47 |  |  | 0.47 | 0.45
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.7 | 19.5 | 20.1 | 19 | 19.5 |  | 19.8 |  |  | 20.1 | 19.2
| LIQUID LEVEL | mm | mm |  | 197.1 | 133.4 | 133 | 209.6 | 211.5 |  | 206.8 |  |  | 201.2 | 193.2
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.86 | 4.83 | 5.41 | 5.61 | 5.55 |  | 5.49 |  |  | 5.03 | 5.5
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 25
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  |  | OK |  | OK | OK | OK | OK | OK |  |  | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 70.1 |  | 76.8 | 72.6 | 62.8 | 74.6 | 73.9 |  |  | 77.4 | 77.7
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 |  | 0 | 0 | 0 | 0.1 | 0.1 |  |  | 0 | 0.2
OPENING OF 2nd VANE |  | % | 0~100% |  | 67.1 |  | 72.1 | 69.1 | 57.9 | 69.7 | 69.1 |  |  | 72.4 | 72.5
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 64.1 |  | 66.3 | 62 | 61.4 | 64.4 | 65.3 |  |  | 71 | 71.5
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 55.3 |  | 72.1 | 40.1 | 40.6 | 36 | 35.9 |  |  | 42.6 | 40.7
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 |  |  | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 114.9 |  | 115.5 | 119.1 | 105.1 | 120 | 115.6 |  |  | 119.2 | 115.7
| INPUT | Kw | 1194kW |  | 1124 |  | 1169 | 1212 | 1068 | 1232 | 1183 |  |  | 1224 | 1180
COMPRESSOR | RUNNING TIME | Hr | NA |  | 45992.3 |  | 46773.1 | 44543.1 | 44524.1 | 46795 | 46785.2 |  |  | 47906.2 | 47889.3
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 57.8 |  | 58.7 | 57.7 | 57.9 | 57.4 | 57.3 |  |  | 59.5 | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.51 |  | 0.49 | 0.59 | 0.58 | 0.54 | 0.59 |  |  | 0.49 | 0.47
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.2 |  | 45.1 | 45 | 46.1 | 44 | 45.1 |  |  | 44.8 | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.22 |  | 0.21 | 0.23 | 0.28 | 0.23 | 0.22 |  |  | 0.23 | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 3.4 |  | 3.2 | 4.7 | 3.7 | 4.9 | 3.9 |  |  | 4.8 | 3.6
| SATURATION TEMPERATURE | CELCIUS | C |  | 3 |  | 2.4 | 4 | 2.9 | 3.9 | 2.8 |  |  | 3.8 | 2.8
| APPROACH TEMP | CELCIUS | C | 0 | 0.6 | 0 | 0.9 | 0.1 | 0.3 | 0.4 | 0 | 0 | 0 | 0.8 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 660.56 |  | 649.12 | 705.9 | 651.68 | 746.1 | 669.68 |  |  | 735.5 | 655.36
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.4 |  | 12.4 | 13.4 | 11.6 | 13.1 | 12.7 |  |  | 13.2 | 12.6
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4 |  | 4.1 | 4.8 | 4 | 5.3 | 3.9 |  |  | 5.6 | 4.3
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.4 | 0 | 8.3 | 8.6 | 7.6 | 7.8 | 8.8 | 0 | 0 | 7.6 | 8.3
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6407.2794 | 0 | 6221.358 | 7010.0924 | 5719.1316 | 6720.0693 | 6805.0624 | 0 | 0 | 6454.7344 | 6281.164
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.79 |  | 0.83 | 0.85 | 0.79 | 0.83 | 0.82 |  |  | 0.85 | 0.85
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.1 |  | 35.9 | 37.2 | 35 | 38.6 | 36.6 |  |  | 37.5 | 35.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.5 |  | 36.9 | 37.9 | 35.4 | 38.6 | 36.7 |  |  | 37.5 | 35.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 1.9 | 0 | 4.3 | 2.7 | 0 | 3.4 | 3.4 | 0 | 0 | 2.2 | 2.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.7 |  | 27.6 | 29.5 | 27.7 | 29.5 | 27.7 |  |  | 29.3 | 27.5
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 33.6 |  | 32.6 | 35.2 | 35.4 | 35.2 | 33.3 |  |  | 35.3 | 33.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.9 | 0 | 5 | 5.7 | 7.7 | 5.7 | 5.6 | 0 | 0 | 6 | 6
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1220.1 |  | 1259.58 | 1303 | 1288.98 | 1221.5 | 1196.86 |  |  | 1228.3 | 1210.72
| HEAT CAPACITY | kW | 8226.9 | 0 | 8312.4596 | 0 | 7272.4018 | 8576.3279 | 11460.9076 | 8039.8961 | 7739.5104 | 0 | 0 | 8510.1617 | 8388.3603
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.45 |  | 0.45 | 0.47 | 0.45 | 0.49 | 0.46 |  |  | 0.48 | 0.45
| SATURATED TEMPERATURE | CELCIUS | C |  | 18.9 |  | 19 | 20.2 | 18.9 | 21.2 | 19.7 |  |  | 20.8 | 19.2
| LIQUID LEVEL | mm | mm |  | 198.4 |  | 122.8 | 204.8 | 194.9 | 205.3 | 203.6 |  |  | 200.8 | 195.3
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.86 |  | 5.47 | 5.06 | 5.72 | 4.7 | 5.41 |  |  | 4.67 | 5.26
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 26
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK |  | OK |  |  | OK | OK
OPENING OF VANE |  | % | 0~100% | 70.1 | 70.1 | 77 | 77 |  | 72.6 |  | 74.1 |  |  | 76 | 76
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0 | 0 | 0.2 | 0.7 |  | 0 |  | 0.1 |  |  | 0.3 | 0.3
OPENING OF 2nd VANE |  | % | 0~100% | 64 | 64 | 72.1 | 72.3 |  | 69.1 |  | 68.5 |  |  | 70.7 | 70.7
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 69.2 | 66.7 | 70.6 | 68 |  | 62.9 |  | 66.5 |  |  | 74.7 | 74.7
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 58.8 | 56.4 | 48.6 | 49 |  | 36.6 |  | 35.9 |  |  | 42.1 | 43.1
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 |  |  | 6.6 | 6.6
| CURRENT | A | ≤115A | 117.4 | 117.2 | 117.4 | 118.6 |  | 116.5 |  | 119.8 |  |  | 116.6 | 119.3
| INPUT | Kw | 1194kW | 1161 | 1153 | 1197 | 1205 |  | 1183 |  | 1223 |  |  | 1190 | 1218
COMPRESSOR | RUNNING TIME | Hr | NA | 46011.2 | 46002 | 46797.3 | 46788.1 |  | 44555.6 |  | 46806 |  |  | 47925.9 | 47916.7
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.4 | 60.2 | 59.3 | 58.9 |  | 58 |  | 57.3 |  |  | 59.3 | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.53 | 0.52 | 0.5 | 0.5 |  | 0.59 |  | 0.54 |  |  | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 45.1 | 46.4 | 44.7 | 45 |  | 44.9 |  | 45 |  |  | 45 | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.24 | 0.23 | 0.22 | 0.23 |  | 0.23 |  | 0.23 |  |  | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.8 | 4.7 | 4.1 | 4.2 |  | 4.2 |  | 5 |  |  | 4.3 | 5
| SATURATION TEMPERATURE | CELCIUS | C | 4.4 | 4.4 | 3.1 | 3.4 |  | 3.6 |  | 4 |  |  | 3.5 | 4
| APPROACH TEMP | CELCIUS | C | 0.7 | 0.7 | 2.2 | 1.4 | 0 | 0.1 | 0 | 0.3 | 0 | 0 | 0.8 | 0.7
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 722.9 | 730 | 668.2 | 699 |  | 660 |  | 703 |  |  | 645.7 | 642
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 13.5 | 13.3 | 13.6 | 13.4 |  | 13 |  | 13.6 |  |  | 13.8 | 13.7
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 5.5 | 5.4 | 6.3 | 5.6 |  | 4.3 |  | 5.3 |  |  | 5.1 | 5.7
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 8 | 7.9 | 7.3 | 7.8 | 0 | 8.7 | 0 | 8.3 | 0 | 0 | 8.7 | 8
| CHILLING CAPACITY | kW | 7032.6kW | 6678.06 | 6659.3533 | 5632.6328 | 6295.843 | 0 | 6630.485 | 0 | 6737.7598 | 0 | 0 | 6486.8245 | 5930.7159
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.83 | 0.83 | 0.86 | 0.86 |  | 0.84 |  | 0.83 |  |  | 0.82 | 0.83
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.6 | 36.7 | 37.4 | 37.6 |  | 36.9 |  | 38.5 |  |  | 36.7 | 37.4
| SATURATED TEMEPRATURE | CELCIUS | C | 37 | 37.2 | 38.2 | 38.6 |  | 37.6 |  | 38.5 |  |  | 36.9 | 37.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.1 | 2.1 | 4.2 | 4.2 | 0 | 2.7 | 0 | 3.5 | 0 | 0 | 2.4 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.9 | 29.2 | 28.7 | 29.1 |  | 29.3 |  | 29.3 |  |  | 28.6 | 29.2
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.9 | 35.1 | 34 | 34.4 |  | 34.9 |  | 35 |  |  | 34.5 | 35.2
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 6 | 5.9 | 5.3 | 5.3 | 0 | 5.6 | 0 | 5.7 | 0 | 0 | 5.9 | 6
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1206.7 | 1218 | 1242 | 1256 |  | 1283 |  | 1190 |  |  | 1191.5 | 1211
| HEAT CAPACITY | kW | 8226.9 | 8360.5081 | 8298.1524 | 7601.1547 | 7686.836 | 0 | 8296.5358 | 0 | 7832.5635 | 0 | 0 | 8117.6097 | 8390.3002
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.48 | 0.48 | 0.47 | 0.48 |  | 0.46 |  | 0.48 |  |  | 0.47 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 20.5 | 20.5 | 20.3 | 20.5 |  | 19.5 |  | 20 |  |  | 20.4 | 20.3
| LIQUID LEVEL | mm | mm | 206.7 | 209.8 | 124.8 | 120.3 |  | 211.3 |  | 212.7 |  |  | 200.9 | 198.1
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.14 | 5.14 | 5.13 | 4.8 |  | 5.47 |  | 4.99 |  |  | 5.41 | 4.89
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 27
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK | OK | OK |  | OK |  | OK |  |  | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 70.2 |  | 77 |  |  |  | 74.1 |  | 74.8 |  | 76.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0 |  | 0.1 |  |  |  | 0.1 |  | 0 |  | 0.3
OPENING OF 2nd VANE |  | % | 0~100% |  | 64 |  | 72.3 |  |  |  | 36.9 |  | 69.1 |  | 70.8
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 67.1 |  | 69.4 |  |  |  | 68.6 |  | 73.3 |  | 74.9
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 51.4 |  | 54.1 |  |  |  | 36.9 |  | 69.8 |  | 42.6
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 |  | 6.6 |  |  |  | 6.6 |  | 6.6 |  | 6.6
| CURRENT | A | ≤115A |  | 114.9 |  | 115.8 |  |  |  | 118.2 |  | 118.8 |  | 116.9
| INPUT | Kw | 1194kW |  | 1138.4 |  | 1175.8 |  |  |  | 1202.9 |  | 1204.3 |  | 1183.1
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46026 |  | 46812 |  |  |  | 46815 |  | 46099 |  | 47940
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 58.2 |  | 59.2 |  |  |  | 57.3 |  | 58.9 |  | 59.2
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 |  | 0.49 |  |  |  | 0.53 |  | 0.53 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 |  | 44.8 |  |  |  | 44.9 |  | 44.6 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 |  | 0.22 |  |  |  | 0.23 |  | 0.23 |  | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 |  | 3.9 |  |  |  | 4.8 |  | 4.9 |  | 4.4
| SATURATION TEMPERATURE | CELCIUS | C |  | 3.9 |  | 2.8 |  |  |  | 3.6 |  | 3.7 |  | 3.5
| APPROACH TEMP | CELCIUS | C |  |  | 0 | 1.1 | 0 | 0 | 0 | -0.1 | 0 | -0.1 | 0 | 0.8
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 718.24 |  | 699.04 |  |  |  | 720.8 |  | 731.6 |  | 708.96
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 12.9 |  | 12.9 |  |  |  | 13.2 |  | 12.9 |  | 13.1
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 4.8 |  | 5 |  |  |  | 4.7 |  | 4.8 |  | 5.2
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8.1 | 0 | 7.9 | 0 | 0 | 0 | 8.5 | 0 | 8.1 | 0 | 7.9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6717.9492 | 0 | 6376.9238 | 0 | 0 | 0 | 7074.8268 | 0 | 6842.9099 | 0 | 6467.418
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.79 |  | 0.83 |  |  |  | 0.82 |  | 0.81 |  | 0.8
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 35.3 |  | 36.2 |  |  |  | 36.9 |  | 35.9 |  | 35.6
| SATURATED TEMEPRATURE | CELCIUS | C |  | 35.4 |  | 36.9 |  |  |  | 36.6 |  | 36.2 |  | 35.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.8 | 0 | 4.8 | 0 | 0 | 0 | 4.3 | 0 | 3.3 | 0 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 27.1 |  | 27 |  |  |  | 26.7 |  | 26.8 |  | 27.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 32.6 |  | 32.1 |  |  |  | 32.3 |  | 32.9 |  | 32.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 0 | 5.1 | 0 | 0 | 0 | 5.6 | 0 | 6.1 | 0 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1263.08 |  | 1298.78 |  |  |  | 1234.52 |  | 1078.42 |  | 1249.36
| HEAT CAPACITY | kW | 8226.9 | 0 | 8021.8707 | 0 | 7648.7044 | 0 | 0 | 0 | 7983.0393 | 0 | 7596.261 | 0 | 7934.7344
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 |  | 0.46 |  |  |  | 0.47 |  | 0.46 |  | 0.46
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.5 |  | 19.4 |  |  |  | 21.2 |  | 19.7 |  | 19.8
| LIQUID LEVEL | mm | mm |  | 185.5 |  | 131 |  |  |  | 192.6 |  | 158.1 |  | 198.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.47 |  | 4.97 |  |  |  | 5.09 |  | 4.9 |  | 5.05
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 28
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  |  | OK | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% | 71.2 | 71.3 |  | 74 |  |  | 74.1 | 74.1 |  | 74 | 78.2 | 78.2
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.7 | 0.6 |  | 0.5 |  |  | 0.1 | 0.1 |  | 0 | 0.3 | 0.3
OPENING OF 2nd VANE |  | % | 0~100% | 66 | 65.8 |  | 68.6 |  |  | 69.1 | 69.1 |  | 68.4 | 72.9 | 72.9
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 63.5 | 65.8 |  | 68.3 |  |  | 63.9 | 66.7 |  | 72.2 | 70.4 | 73.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 56.9 | 51.4 |  | 51.4 |  |  | 35.9 | 33.8 |  | 52.8 | 40.2 | 44.5
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  |  | 6.6 | 6.6 |  | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A | 116.2 | 119 |  | 116.9 |  |  | 118 | 118.3 |  | 118.9 | 118.2 | 119.1
| INPUT | Kw | 1194kW | 1158 | 1172 |  | 1185 |  |  | 1210 | 1215 |  | 1216 | 1205 | 1219
COMPRESSOR | RUNNING TIME | Hr | NA | 46045.6 | 46035.8 |  | 46834.2 |  |  | 46849.6 | 46839.7 |  | 46118.1 | 47960.3 | 47950.5
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.4 | 58.4 |  | 59.1 |  |  | 57.2 | 57.2 |  | 58.7 | 59.2 | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.53 |  | 0.5 |  |  | 0.53 | 0.54 |  | 0.53 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 44.8 |  | 45 |  |  | 45 | 45.8 |  | 45.2 | 45.1 | 45.1
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.23 | 0.28 |  | 0.23 |  |  | 0.23 | 0.28 |  | 0.2 | 0.23 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C | 4.4 | 4.8 |  | 4.3 |  |  | 4.6 | 4.6 |  | 4.9 | 4.2 | 4.5
| SATURATION TEMPERATURE | CELCIUS | C | 3.8 | 4.2 |  | 3.4 |  |  | 3.5 | 3.6 |  | 3.8 | 3.7 | 3.5
| APPROACH TEMP | CELCIUS | C | 1 | 0.6 | 0 | 1.7 | 0 | 0 | 1.3 | 1.1 | 0 | 1 | 1.4 | 1.6
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 747 | 726.88 |  | 706.56 |  |  | 742.4 | 720.4 |  | 735.68 | 731.6 | 708.72
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12.6 | 12.8 |  | 12.8 |  |  | 12.7 | 13.1 |  | 12.8 | 12.9 | 12.9
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.8 | 4.8 |  | 5.1 |  |  | 4.8 | 4.7 |  | 4.8 | 5.1 | 5.1
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.8 | 8 | 0 | 7.7 | 0 | 0 | 7.9 | 8.4 | 0 | 8 | 7.8 | 7.8
| CHILLING CAPACITY | kW | 7032.6kW | 6728.1755 | 6714.8268 | 0 | 6282.3464 | 0 | 0 | 6772.4711 | 6987.7136 | 0 | 6796.1201 | 6589.4688 | 6383.3903
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.82 | 0.82 |  | 0.85 |  |  | 0.85 | 0.85 |  | 0.84 | 0.83 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 36.4 | 36.4 |  | 37.1 |  |  | 37.9 | 37.5 |  | 36.7 | 36.7 | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C | 36.7 | 36.6 |  | 37.8 |  |  | 37.8 | 37.5 |  | 37.1 | 36.8 | 36.5
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2 | 3 | 0 | 4.8 | 0 | 0 | 3.3 | 4.2 | 0 | 3.2 | 2.3 | 2.9
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 28.8 | 28.3 |  | 28.1 |  |  | 28.8 | 27.8 |  | 27.9 | 28.6 | 28.1
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 34.7 | 33.6 |  | 33 |  |  | 34.5 | 33.3 |  | 33.9 | 34.5 | 33.6
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.9 | 5.3 | 0 | 4.9 | 0 | 0 | 5.7 | 5.5 | 0 | 6 | 5.9 | 5.5
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1200.6 | 1264.2 |  | 1302.84 |  |  | 1202.3 | 1247.96 |  | 1094.94 | 1219.9 | 1261.68
| HEAT CAPACITY | kW | 8226.9 | 8179.6074 | 7737.0208 | 0 | 7371.7275 | 0 | 0 | 7913.5219 | 7925.843 | 0 | 7586.1894 | 8311.097 | 8012.9792
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.47 | 0.47 |  | 0.47 |  |  | 0.48 | 0.48 |  | 0.47 | 0.47 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 20 | 20 |  | 20.2 |  |  | 20.3 | 20.6 |  | 20.3 | 20.1 | 20.3
| LIQUID LEVEL | mm | mm | 184.9 | 171.7 |  | 119.3 |  |  | 209.5 | 207 |  | 170.8 | 205.9 | 204.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 4.92 | 5 |  | 4.78 |  |  | 4.85 | 4.99 |  | 4.86 | 4.78 | 4.78
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 29
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  |  | OK | OK |  | OK | OK | OK
OPENING OF VANE |  | % | 0~100% |  | 70.1 | 80.3 | 74.8 |  |  |  | 72.2 | 73.4 | 73.5 | 75.6 | 75.6
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% |  | 0.6 | 0 | 0 |  |  |  | 0.1 | 0 | 0 | 0.3 | 0.3
OPENING OF 2nd VANE |  | % | 0~100% |  | 67.1 | 76.3 | 69.6 |  |  |  | 67.5 | 67.9 | 67.8 | 71.1 | 71
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% |  | 64.1 | 69.7 | 67.7 |  |  |  | 65.6 | 75.6 | 71.7 | 76.8 | 73
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% |  | 55.3 | 55.8 | 50.1 |  |  |  | 35.3 | 60.1 | 67.8 | 43.6 | 40
MOTOR | VOLTAGE | V | 6600V(± 5% ) |  | 6.6 | 6.6 | 6.6 |  |  |  | 6.6 | 6.6 | 6.6 | 6.6 | 6.6
| CURRENT | A | ≤115A |  | 114.9 | 118.9 | 115.8 |  |  |  | 118.2 | 118.5 | 159.8 | 116.6 | 118
| INPUT | Kw | 1194kW |  | 1150 | 1213 | 1179 |  |  |  | 1200 | 1220 | 1208 | 1188 | 1199
COMPRESSOR | RUNNING TIME | Hr | NA |  | 46060 | 46852 | 46844 |  |  |  | 46861 | 46136 | 46128 | 47980 | 47972
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C |  | 57.8 | 59.4 | 58.8 |  |  |  | 57.2 | 58.7 | 58.9 | 59.3 | 59.4
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure |  | 0.52 | 0.49 | 0.5 |  |  |  | 0.54 | 0.46 | 0.48 | 0.48 | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC |  | 45.1 | 45.1 | 45 |  |  |  | 45 | 44.8 | 44.9 | 45.1 | 44.8
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa |  | 0.23 | 0.23 | 0.22 |  |  |  | 0.23 | 0.24 | 0.23 | 0.24 | 0.23
| EVAPORATING TEMPERATURE | CELCIUS | C |  | 4.6 | 3.9 | 4 |  |  |  | 4.6 | 5.5 | 4.9 | 4.8 | 4.4
| SATURATION TEMPERATURE | CELCIUS | C |  | 4 | 36.5 | 3.2 |  |  |  | 3.7 | 4.5 | 3.5 | 3.9 | 3.8
| APPROACH TEMP | CELCIUS | C |  | 1 | 1.7 | 3.2 | 0 | 0 | 0 | 1.3 | 0.2 | 1.5 | 1.7 | 1.6
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h |  | 723.44 | 722.96 | 704.24 |  |  |  | 721.68 | 758.88 | 728 | 684.72 | 705.6
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 |  | 13 | 13.6 | 13.1 |  |  |  | 13.5 | 13.5 | 13.2 | 13.7 | 13.3
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 |  | 5 | 5.6 | 6.4 |  |  |  | 5 | 5.7 | 5 | 5.6 | 5.4
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 0 | 8 | 8 | 6.7 | 0 | 0 | 0 | 8.5 | 7.8 | 8.2 | 8.1 | 7.9
| CHILLING CAPACITY | kW | 7032.6kW | 0 | 6683.0485 | 6678.6143 | 5448.5081 | 0 | 0 | 0 | 7083.4642 | 6835.1778 | 6893.3025 | 6404.4249 | 6436.7667
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) |  | 0.82 | 0.86 | 0.86 |  |  |  | 0.85 | 0.83 | 0.81 | 0.81 | 0.82
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C |  | 36.1 |  | 37.1 |  |  |  | 37.5 | 35.9 | 36.9 | 35.6 | 36.5
| SATURATED TEMEPRATURE | CELCIUS | C |  | 36.4 | 37.9 | 38 |  |  |  | 37.6 | 36.8 | 37.3 | 36.1 | 36.6
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 0 | 2.2 | 5 | 4.3 | 0 | 0 | 0 | 3.4 | 3.3 | 2.4 | 3 | 0.1
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 |  | 28.7 | 27.8 | 29 |  |  |  | 28.7 | 27.5 | 28.7 | 27.8 | 28.6
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 |  | 34.2 | 32.9 | 33.7 |  |  |  | 34.2 | 33.5 | 34.9 | 33.1 | 36.5
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 0 | 5.5 | 5.1 | 4.7 | 0 | 0 | 0 | 5.5 | 6 | 6.2 | 5.3 | 7.9
| COOLING WATER FLOW RATE | m3/h | 1273.1 |  | 1265 | 1287.86 | 1300.6 |  |  |  | 1243.06 | 1122.1 | 1087.24 | 1290.8 | 1263.64
| HEAT CAPACITY | kW | 8226.9 | 0 | 8034.0647 | 7584.3949 | 7058.6836 | 0 | 0 | 0 | 7894.7229 | 7774.3649 | 7783.9353 | 7899.8152 | 11527.4319
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa |  | 0.46 | 0.46 | 0.47 |  |  |  | 0.48 | 0.47 | 0.47 | 0.47 | 0.47
| SATURATED TEMPERATURE | CELCIUS | C |  | 19.8 | 19.6 | 20.2 |  |  |  | 20 | 20.1 | 20.4 | 20 | 20.2
| LIQUID LEVEL | mm | mm |  | 187.8 | 127 | 128.8 |  |  |  | 201 | 159.5 | 159.8 | 198.8 | 198.7
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 |  | 5.52 | 6.1 | 5.12 |  |  |  | 5 | 4.86 | 4.98 | 5.09 | 4.82
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO

## 30
| OPERATION CHILLER LOG SHEET & REFRIGERANT LEAK | [10 empty] | REVISION : 1
[12 empty] | DOC NO : | OPER-01-QR-01
OPERATOR :
PAGE : 1 OF 1
OPERATION DATE
CHILLER |  |  | CONTROL LIMIT | EC0120A |  | EC0120B |  | EC0120C |  | EC0120D |  | EC0120E |  | EC0120F
TIME |  |  |  | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00 | 9:00 | 00:00
REFRIGERANT LEAK STATUS |  | OK / NOT OK |  | OK | OK |  | OK |  |  | OK | OK | OK | OK |  | OK
OPENING OF VANE |  | % | 0~100% | 72 | 72 |  | 75.1 |  |  | 74.1 | 74.1 | 72.6 | 72.4 |  | 75
OPENING HOT GAS BYPASS VALVE |  | % | 0~100% | 0.6 | 0.6 |  | 0 |  |  | 0.1 | 0.1 | 0 | 0 |  | 0.3
OPENING OF 2nd VANE |  | % | 0~100% | 67.1 | 66.9 |  | 70.1 |  |  | 69.1 | 69.1 | 67.3 | 67.2 |  | 69.4
OPENING OF HIGH-STAGE EXPANSION VALVE |  | % | 0~100% | 63.1 | 64.2 |  | 66.1 |  |  | 64.5 | 63.8 | 68.8 | 69.1 |  | 71.4
OPENING OF LOW-STAGE EXPANSION VALVE |  | % | 0~100% | 53.4 | 48.1 |  | 53.8 |  |  | 36.6 | 33.7 | 55.5 | 55.8 |  | 38.8
MOTOR | VOLTAGE | V | 6600V(± 5% ) | 6.6 | 6.6 |  | 6.6 |  |  | 6.6 | 6.6 | 6.6 | 6.6 |  | 6.6
| CURRENT | A | ≤115A | 115.9 | 118.3 |  | 116.4 |  |  | 117.5 | 117.2 | 116.2 | 116.4 |  | 115.3
| INPUT | Kw | 1194kW | 1141 | 1156 |  | 1176 |  |  | 1196 | 1201 | 1185 | 1192 |  | 1176
COMPRESSOR | RUNNING TIME | Hr | NA | 46078.9 | 46070 |  | 46866.4 |  |  | 46879.3 | 46870.3 | 46159.5 | 46150.6 |  | 47993.9
| SUCTION TEMPERATURE | CELCIUS | C
| DISCHARGE TEMPERATURE | CELCIUS | 35 -70 degC
| OIL TANK OIL TEMPERATURE | CELCIUS | 45-72 deg C | 58.1 | 58 |  | 58.8 |  |  | 57.2 | 57.3 | 58.5 | 58.6 |  | 59.3
| OIL PRESSURE | Mpa(G) | Diff pressure 0.25-0.35 Mpa OIL -EVAP =Diff pressure | 0.52 | 0.52 |  | 0.49 |  |  | 0.53 | 0.53 | 0.48 | 0.48 |  | 0.48
OIL LEVEL
| OIL SUPPLY TEMPERATURE | CELCIUS | 35-45 degC | 44.9 | 45.1 |  | 45 |  |  | 45 | 44.9 | 45 | 45 |  | 45
EVAPORATOR | EVAPORATING PRESSURE | Mpa(G) | ≥0.18Mpa | 0.28 | 0.23 |  | 0.22 |  |  | 0.22 | 0.22 | 0.28 | 0.23 |  | 0.22
| EVAPORATING TEMPERATURE | CELCIUS | C | 3.9 | 4.3 |  | 3.8 |  |  | 4.3 | 4.4 | 4.6 | 4.6 |  | 4.2
| SATURATION TEMPERATURE | CELCIUS | C | 3.5 | 3.9 |  | 2.9 |  |  | 3.4 | 3.8 | 3.9 | 3.6 |  | 3.8
| APPROACH TEMP | CELCIUS | C | 0.8 | 1.1 | 0 | 2 | 0 | 0 | 1.1 | 0.9 | 0.7 | 1.2 | 0 | 1.2
| CHILLED WATER FLOW RATE | m3/h | 634.8 m3h | 749.28 | 728.4 |  | 700.6 |  |  | 744.32 | 721.2 | 756.96 | 731.4 |  | 708.8
| CHILLED WATER ENTERING TEMPERATURE | CELCIUS | 13.5 | 12 | 13 |  | 12.7 |  |  | 12.5 | 12.7 | 12.2 | 12.7 |  | 12.9
| CHILLED WATER LEAVING TEMPERATURE | CELCIUS | 4 | 4.3 | 5 |  | 4.9 |  |  | 4.5 | 4.7 | 4.6 | 4.8 |  | 5
| TEMPERATURE DIFFERENCE | CELCIUS | 9.5 | 7.7 | 8 | 0 | 7.8 | 0 | 0 | 8 | 8 | 7.6 | 7.9 | 0 | 7.9
| CHILLING CAPACITY | kW | 7032.6kW | 6662.1894 | 6728.8684 | 0 | 6310.254 | 0 | 0 | 6875.9353 | 6662.3557 | 6643.067 | 6672.1247 | 0 | 6465.9584
CONDENSOR | CONDENSING PRESSURE | Mpa(G) | ≤1.01Mpa(G) | 0.8 | 0.82 |  | 0.85 |  |  | 0.83 | 0.81 | 0.82 | 0.81 |  | 0.81
| CONSENSED LIQUID TEMPERATURE | CELCIUS | C | 35.1 | 36 |  | 36.8 |  |  | 36.6 | 37.5 | 35.8 | 36.5 |  | 36.2
| SATURATED TEMEPRATURE | CELCIUS | C | 35.6 | 36.4 |  | 37.7 |  |  | 36.8 | 37.4 | 36.2 | 36.9 |  | 36.3
| APPROACH TEMP (COND LQ TEMP - LEAVING TEMP) | CELCIUS |  | 2.9 | 2.1 | 0 | 4.2 | 0 | 0 | 4.3 | 3.4 | 3.2 | 2.4 | 0 | 2.3
| LIQUID LEVEL(Side Glass Bottom) | mm
| COOLING WATER ENTERING TEMPERATURE | CELCIUS | 30.8 | 27.5 | 38.7 |  | 28.5 |  |  | 27.3 | 28.5 | 27.3 | 28.4 |  | 28.4
| COOLING WATER LEAVING TEMPERATURE | CELCIUS | 36.4 | 32.7 | 34.3 |  | 33.5 |  |  | 32.5 | 34 | 33 | 34.5 |  | 34
| TEMPERATURE DIFFERENCE COOLING WATER | CELCIUS | 5.6 | 5.2 | -4.4 | 0 | 5 | 0 | 0 | 5.2 | 5.5 | 5.7 | 6.1 | 0 | 5.6
| COOLING WATER FLOW RATE | m3/h | 1273.1 | 1295.42 | 1259.4 |  | 1305.5 |  |  | 1294.86 | 1245.9 | 1135.68 | 1089.2 |  | 1269.1
| HEAT CAPACITY | kW | 8226.9 | 7778.5035 | -6398.7991 | 0 | 7537.5289 | 0 | 0 | 7775.1409 | 7912.7598 | 7475.03 | 7672.194 | 0 | 8206.6513
ECONOMIZER | ECONOMIZER PRESSURE | Mpa(G) | Mpa | 0.45 | 0.46 |  | 0.46 |  |  | 0.47 | 0.47 | 0.46 | 0.47 |  | 0.47
| SATURATED TEMPERATURE | CELCIUS | C | 19.2 | 19.6 |  | 19.9 |  |  | 19.8 | 20 | 19.5 | 19.9 |  | 20.2
| LIQUID LEVEL | mm | mm | 202.7 | 168.5 |  | 121.2 |  |  | 211.8 | 211.6 | 165.4 | 158 |  | 199.6
HEAT BALANCE |  |  | 0.95~1.05
COP |  |  | 5.89 | 5.12 | 5.22 |  | 4.89 |  |  | 4.88 | 4.94 | 4.8 | 5 |  | 5
% OF COOLING CAPACITY
% OF MOTOR INPUT
REMARK : | CHILLER :
Differential pressure of Oil pressure - Evap pressure is in range 0.25 Mpa ~ 0.35 Mpa.
* Movement of Expansion Valve motor operation depends on running condition.
| REFRIGERANT ALARM |  |  | FALSE | CHILLER ALARM :
| REFRIGERANT ALARM |  |  | YES | NO